## Sheet1
DSA Tool - Test Sytem Characterization
Name: | "10 machine New-England Power System”modified to meet the purpose of the ATTEST T4.6 Task (DSA Tool)
Transmission System Nominal Voltages | 345 kV, 230 kV & 138 kV
Fn (Nominal Frequency) | 60 Hz
Nr. Of Buses | 42
Nr. Loads | 31
Nr. Lines | 34
Nr. Of 2 Windings Transf. | 15 (3 Transmssion transf. and 12 generators step up transf.)
Nr. Of SGs | 7
Nr. Of SCs | 3 | Total of 2500 MVA: SC1 - 800 MVA; SC2 -700 MVA; SC3 - 1000 MVA
RES | 3 WFs | Total of 2500 MW: WF1 - 800 MW; WF2 - 700 MW; WF3 - 1000 MW
DSA Tool - Internal Block 1 (OPs Generation and Critical Disturbances Identification)
Nr. OPs Generated | 534000
Load Range (OPs) | [2700, 8060] MW --> OPs generated in 20 MW steps
WFs Active Power Range (OPs) | [0, 2500] MW | --> OPs generated in 20 MW steps
Critical Contingencies/Disturbances identified:
Contingency id 1 | three phase symmetrical short circuit at bus 16 (Zf≈0 and fault clearing time = 250 ms)
Contingency id 2 | three phase symmetrical short circuit at bus 31 (Zf≈0 and fault clearing time = 250 ms)
Contingency id 3 | three phase symmetrical short circuit at bus 2 (Zf≈0 and fault clearing time = 250 ms)
DSA Tool - Internal Block 2 (Generation of functional knowledge through time-domain dynamic simulations)
In average 85% of OPs are likely to be secure for all the disturbances analysed
In average 15% of OPs might be unsecure (system security may be at at risk regarding dynamic frequency stability (violations in freq. nadir and/or RoCOF regulated values)
DSA Tool - Internal Block 3 (ANN Model/Architecture and Training Process )
ANN model tyoe | Feed-forward ANN- Sequential model (linear stack of layers)
Nr. of hidden ayers | 1
Nr. Of hidden neurons | 12
Activation Function (Hidden layer) | Sigmoid
Activation Function (Output layer) | Linear
Training Algorithm | Adam optimization algorithm using Early Stopping Criterion to avoid overfitting("patiente" parameter set to 20)
Standardization/Normalization Process | Normalization between [0,1] using Min-Max Method
Implementation of the ANN model and of the training algorithm | Python TensorFlow package (Keras Library)
Training set | 373800
Validation set | 80100
Test set | 80100