## TII - ManualEx
System | Description | Redundancy | Function Blocks | Failure Modules | States | Transitions | Time Resolution | Iterations | Analysis Time | Result | RBD
RailRoad Crossing System | 3-Track RailRoad crossing system with track sensors and gate. | Nil | 7 | 5 | 69362 | 184326 | 10ms | 360000 | 361s | 0.00022848 | 0.00024616
Gas Detection System | Hazardous hydrocarbon gas detection system with redundant sensors. | Sensors 1oo2 | 6 | 4 | 64649 | 130994 | 10ms | 360000 | 243s | 0.00022917 | 0.0002293
Boiler System | Detection and prevention of pressure overload scenario. | Sensors 1oo2 | 7 | 4 | 44114 | 107136 | 10ms | 360000 | 140s | 3.5721e-07 | 2.8738e-05
Fire Detection and Supression System | 3 Smoke sensors and 1 alarm and 1 valve-controlled sprinkler system. | Nil | 9 | 6 | 41363 | 113314 | 10ms | 360000 | 304s | 7.8925e-05 | 0.00025341
RailRoad Crossing DCDS07 | Single track wireless link crossing with traffic signal and train model. | Nil | 7 | 5 | 2648 | 9939 | 10ms | 360001 | 21s | 2.3104e-05 | 9.5911e-05

## RBD
Fire Detection and Suppression System |  | Quantity | f/h
Detector: | 5.62e-06 | 3 series | 1.686e-05 | 3 * 5.62E-06
Alarm: | 0.0002283 | 1 | 0.0002283
Valve: | 7.268e-06 | 1 | 7.268e-06
PLC: | 1e-06 | 1 | 1e-06
RBD |  |  | 0.00025343
Boiler System
Flow | 7.279e-06 | 1oo2 | 5.2998e-11 | 1 - (1 - ((1-e^(-7.28E-6)) *(1-e^(-7.28E-6))))
Valve | 7.268e-06 | 1 | 7.268e-06
Pressure | 2.047e-05 | 1 | 2.047e-05
PLC | 1e-06 | 1 | 1e-06
RBD |  |  | 2.8738e-05
RailRoad Crossing System
Track Sensor | 5.62e-06 | 3 series | 1.686e-05 | 3 * 5.62E-06
Gate Motor | 0.0002283 | 1 | 0.0002283
PLC | 1e-06 | 1 | 1e-06
RBD |  |  | 0.00024616
Hydrocarbon Gas Detection System
Gas Detector | 1.028e-05 | 1oo2 | 1.0568e-10 | 1 - (1 - ((1-e^(-10.28E-06)) *(1-e^(-10.28E-06))))
PLC | 1e-06 | 1 | 1e-06
Ventilator Fan | 0.0002283 | 1 | 0.0002283
RBD |  |  | 0.0002293
RailRoad Crossing DCDS07
Radio link | 1e-08 | 2 series | 2e-08 | 2 * 1.00E-08
Signal | 1.028e-07 | 1 | 1.028e-07
Crossing | 2.2998e-05 | 1 | 2.2998e-05
Brake | 7.279e-05 | 1 | 7.279e-05
RBD |  |  | 9.5911e-05