## Information List
Device | Modbus Address (Decimal System) | OD Protocol Address(Prime Index,Sub-index) |  | Definition | Monitoring | Original Value | Data Type | Effective Range | Value/status | Information Property(0 internal,1 external)
DESS | 0 |  |  | System running status |  | 0 | U16 | [0,4] | 0: Initialization 1: Standby 2: Starting 3: Running 4: Fault | 1
BSMU | 1 | 50 | 1 | BSMU Working Status |  | 0 | U16 | [0,10] | 0: Initialization 1: Off-grid 2: Being On-grid 3: On-grid Operation 4: Being Stop 5: Fault 6: Debug Mode 7: Reserved 8: Low Consumption Mode 9: Start Precharging 10: Precharging | 1
| 2 |  | 2 | Stack Charging-discharging Status |  | 0 |  | 0,1,2 | 0: (Standby)Neither Charging nor Discharging 1: Charging 2: Discharging
| 3 |  | 3 | Status of Battery Group Contactors |  | 0 |  | 0,1 | 0: (All)Totally Disconnected 1: Partially Disconnected
| 4 |  | 4 | Battery Group on-grid status |  | 0 |  | [0,65535] | Every Bit Forming One Group 0: Not On-grid 1: On-grid
| 5 |  | 5 | Working Mode of Battery Stack |  | 0 |  | 0,1 | 0: Normal Mode 1: Nominal Mode
| 6 | 80 | 0 | Battery Group Enabling Status |  | 0 | U16 |  | Every Bit Forming One Group 0: Forbidden 1: Enable | 1
| 7 |  | 1 | Isolation Switch Status of Battery Group |  | 0 |  |  | Every Bit Forming One Group 0: Disconnected 1: Connected
| 8 |  | 2 | Isolation Switch Status of PCS Cabinet |  | 0 |  |  | 0: Disconnected 1: Connected bit0: Isolation Switch 1 bit1: Isolation Switch 2
| 9 | 81 | 0 | Enabling Status of Dynamic On-grid |  | 0 | U16 | 0,1 | 0: Forbidden 1: Enabling | 1
| 10 |  | 1 | Dynamic Fault Isolation Enabling Status |  | 0 |  | 0,1 | 0: Forbidden 1: Enabling
| 11 |  | 2 | Minimum Working Groups of Fault Isolated |  | 1 |  | [1,16] | 1
BSMU | 20 | 52 | 0 | PBMS Warning Information0 |  | 0 | U16 | [0,65535] | Refer to Warning List | 1
| 21 |  | 1 | PBMS Warning Information1 |  | 0 |  | [0,65535]
| 22 |  | 2 | PBMS Warning Information2 |  | 0 |  | [0,65535] |  | 0
| 23 |  | 3 | PBMS Warning Information3 |  | 0 |  | [0,65535]
| 24 |  | 4 | PBMS Warning Information4 |  | 0 |  | [0,65535]
| 25 |  | 9 | Distributed Equilibrium Sampling Warning |  | 0 |  | [0,65535]
| 26 |  | 10 | Distributed Equilibrium Control Warning |  | 0 |  | [0,65535]
| 27 |  | 11 | Distributed Warning Reserved |  | 0 |  | [0,65535]
BSMU | 30 | 53 | 0 | PBMS Fault Information0 |  | 0 | U16 | [0,65535] | Refer to Fault List | 1
| 31 |  | 1 | PBMS Fault Information1 |  | 0 |  | [0,65535]
| 32 |  | 2 | PBMS Fault Information2 Reserved |  | 0 |  | [0,65535] |  | 0
| 33 |  | 3 | PBMS Fault Information3 Reserved |  | 0 |  | [0,65535]
| 34 |  | 4 | PBMS Fault Information4 Reserved |  | 0 |  | [0,65535]
| 35 |  | 5 | PBMS Fault Information5 Reserved |  | 0 |  | [0,65535]
| 36 |  | 6 | PBMS Fault Information6 Reserved |  | 0 |  | [0,65535]
| 37 |  | 7 | PBMS Fault Information7 Reserved |  | 0 |  | [0,65535]
| 38 |  | 8 | PBMS Fault Information8 Reserved |  | 0 |  | [0,65535]
| 39 |  | 9 | PBMS Fault Information9 Reserved |  | 0 |  | [0,65535]
BSMU | 40 | 50 | 0 | Protection Status |  | 0 | U16 | [0,4] | 0: Normal 1: Common Warning 2: Serious Warning 3: Common Fault 4: Serious Fault | 0
| 41 | 84 | 0 | Factory Settings Result |  | 0 | U16 | [0,7] | 0: Not Operate 1: Save Successfully 2: Save Failed 3: Save and Verify Failed 4: Restore Successful 5: EEP Parameters Restore Failed 6: Restore Backup Parameters Failed 7: EEP Parameters Modify Abnormal | 0
BECU_0 | 45 | 70 | 0 | Battery Group0 Contactor status |  | 0 | U16 |  | Every Bit Representing One Status 0: Open 1: Close | 1
| 46 |  | 1 | Periphery IO Detection Status of Battery Group0 |  | 0 |  |  | Every Bit Representing One Status 0: Open 1: Close
| 47 | 52 | 5 | BMS0 Warning Information |  | 0 |  | [0,65535] | Refer to Warning List
| 48 | 53 | 10 | BMS0 Fault Information0 |  | 0 |  | [0,65535] | Refer to Fault List
| 49 |  | 11 | BMS0 Fault Information1 |  | 0 |  | [0,65535]
BECU_1 | 50 | 70 | 0 | Battery Group1 Contactor status |  | 0 | U16 |  | Every Bit Representing One Status 0: Open 1: Close
| 51 |  | 1 | Periphery IO Detection Status of Battery Group1 |  | 0 |  |  | Every Bit Representing One Status 0: Open 1: Close
| 52 | 52 | 6 | BMS1 Warning Information |  | 0 |  | [0,65535] | Refer to Warning List
| 53 | 53 | 12 | BMS1 Fault Information0 |  | 0 |  | [0,65535] | Refer to Fault List
| 54 |  | 13 | BMS1 Fault Information1 |  | 0 |  | [0,65535]
BECU_2 | 55 | 70 | 0 | Battery Group0 Contactor status |  | 0 | U16 |  | Every Bit Representing One Status 0: Open 1: Close
| 56 |  | 1 | Periphery IO Detection Status of Battery Group0 |  | 0 |  |  | Every Bit Representing One Status 0: Open 1: Close
| 57 | 52 | 7 | BMS2 Warning Information |  | 0 |  | [0,65535] | Refer to Warning List
| 58 | 53 | 14 | BMS2 Fault Information0 |  | 0 |  | [0,65535] | Refer to Fault List
| 59 |  | 15 | BMS2 Fault Information1 |  | 0 |  | [0,65535]
BECU_3 | 60 | 70 | 0 | Battery Group1 Contactor status |  | 0 | U16 |  | Every Bit Representing One Status 0: Open 1: Close
| 61 |  | 1 | Periphery IO Detection Status of Battery Group1 |  | 0 |  |  | Every Bit Representing One Status 0: Open 1: Close
| 62 | 52 | 8 | BMS3 Warning Information |  | 0 |  | [0,65535] | Refer to Warning List
| 63 | 53 | 16 | BMS3 Fault Information0 |  | 0 |  | [0,65535] | Refer to Fault List
| 64 |  | 17 | BMS3 Fault Information1 |  | 0 |  | [0,65535]
PCS Summary | 100 |  |  | Inverter Overall Operation Status |  | 0 | U16 | [0,5] | 0: Self-inspection 1: Standby 2: Being Startup 3: Off-grid Operation 4: On-grid Operation 5: Fault | 1
PCS_1 | 101 |  |  | Inverter1 Warning Code1 (A-phase, Split phase L1, or Single-phase) |  | 0 | U16 | [0,65535] | Refer to Warning List | 1
| 102 |  |  | Inverter1 Warning Code2 (A-phase, Split phase L1, or Single-phase) |  | 0 |  | [0,65535]
| 103 |  |  | Inverter1 Fault Code1 (A-phase, Split phase L1, or Single-phase) |  | 0 |  | [0,65535] | Refer to Fault List
| 104 |  |  | Inverter1 Fault Code2 (A-phase, Split phase L1, or Single-phase) |  | 0 |  | [0,65535]
| 105 |  |  | Inverter1 Fault Code3 (A-phase, Split phase L1, or Single-phase) |  | 0 |  | [0,65535]
PCS_2 | 106 |  |  | Inverter2 Warning Code1(B-phase, Split phaseL2, Single-phase Reserved) |  | 0 | U16 | [0,65535] | Refer to Warning List
| 107 |  |  | Inverter2 Warning Code2 (B-phase, Split phase L2, Single-phase Reserved) |  | 0 |  | [0,65535]
| 108 |  |  | Inverter2 Fault Code1(B-phase, Split phase L2, Single-phase Reserved) |  | 0 |  | [0,65535] | Refer to Fault List
| 109 |  |  | Inverter2 Fault Code2 (B-phase, Split phase L2, Single-phase Reserved) |  | 0 |  | [0,65535]
| 110 |  |  | Inverter2 Fault Code3 (B-phase, Split Phase L2, Single-phase Reserved) |  | 0 |  | [0,65535]
PCS_3 | 111 |  |  | Inverter3 Warning Code1 (C-phase, Split phase & Single-phase Reserved) |  | 0 | U16 | [0,65535] | Refer to Warning List
| 112 |  |  | Inverter3 Warning Code2 (C-phase, Split phase & Single-phase Reserved) |  | 0 |  | [0,65535]
| 113 |  |  | Inverter3 Fault Code1 (C-phase, Split phase & Single-phase Reserved) |  | 0 |  | [0,65535] | Refer to Fault List
| 114 |  |  | Inverter3 Fault Code2 (C-phase, Split phase & Single-phase Reserved) |  | 0 |  | [0,65535]
| 115 |  |  | Inverter3 Fault Code3 (C-phase, Split phase & Single-phase Reserved) |  | 0 |  | [0,65535]
PV_1 | 120 |  |  | Charger1 Working Status |  | 0 | U16 | 0,1 | 0: Shutdown 1: Working | 1
| 121 |  |  | Charger1 MPPT Status |  | 0 |  | 0,1 | 0: No 1: Yes
| 122 |  |  | Charger1 Charging Status |  | 0 |  | [0,6] | 0: No Charging 1: Fast Charging 2: Absorb Charging 3: Floating Charging 4: Re-floating Charging 5: Limited Power Charging (Battery Full) 6: Limited Power Charging (Over-temperature)
| 123 |  |  | Charger1 Warning Code |  | 0 |  | [0,65535] | Refer to Warning List
| 124 |  |  | Charger1 Fault Code |  | 0 |  | [0,65535] | Refer to Fault List
PV_2 | 125 |  |  | Charger2 Working Status |  | 0 | U16 | 0,1 | 0: Shutdown 1: Working
| 126 |  |  | Charger2 MPPT Status |  | 0 |  | 0,1 | 0: No 1: Yes
| 127 |  |  | Charger2 Charging Status |  | 0 |  | [0,6] | 0: No Charging 1: Fast Charging 2: Absorb Charging 3: Floating Charging 4: Re-floating Charging 5: Limited Power Charging (Battery Full) 6: Limited Power Charging (Over-temperature)
| 128 |  |  | Charger2 Warning Code |  | 0 |  | [0,65535] | Refer to Warning List
| 129 |  |  | Charger2 Fault Code |  | 0 |  | [0,65535] | Refer to Fault List
BSMU | 140 | 70 | 0 | Battery Stack Current |  | 30000 | U16 | [0,60000] | (-30000)0.1A | 1
| 141 |  | 1 | Battery Stack Voltage |  | 0 |  | [0,65535] | 0.1V
| 142 |  | 2 | Battery Stack Power |  | 0 |  | [0,65535] | 0.1KW
| 143 |  | 3 | Battery Stack Overall SOC |  | 0 |  | [0,100] | %
| 144 |  | 6 | Battery Stack SOH |  | 0 |  | [0,100] | %
| 145 | 73 | 1 | Stack Charging Current Limit Value |  | 0 | U16 |  | 0.1A | 1
| 146 |  | 2 | Stack Discharging Current Limit Value |  | 0 |  |  | 0.1A
| 147 |  | 3 | Stack Charging Current Limit Value |  | 0 |  |  | 0.1KW
| 148 |  | 4 | Stack Discharging Power Limit Value |  | 0 |  |  | 0.1KW
| 149 | 81 | 3 | Remote SCI Station Address |  | 1 | U16 | [1,247] | 1 | 1
| 150 |  | 4 | Remote SCI Baud Rate |  | 19200 |  | 4800,9600,19200,38400 | 1
| 151 | 82 | 0 | Battery Stack Historical Charging Energy (High-order) |  | 0 | U16 |  | 1KWH | 1
| 152 |  | 0 | Battery Stack Historical Charging Energy (Low-order) |  | 0
| 153 |  | 1 | Battery Stack Historical Discharging Energy (High-order) |  | 0
| 154 |  | 1 | Battery Stack Historical Discharging Energy (Low-order) |  | 0 |  |  | 1KWH
| 160 | 70 | 4 | Available Group SOC of Battery Stack |  | 0 | U16 | [0,100] | % | 0
| 161 |  | 5 | On-grid Group SOC of Battery Stack |  | 0 |  | [0,100] | %
| 162 | 71 | 0 | Stack Electric Energy that can be charged |  | 0 | U16 |  | 1KWH
| 163 |  | 1 | Stack Electric Energy that can be discharged |  | 0 |  |  | 1KWH(Stack Remain Electric Energy)
| 164 |  | 2 | Nomianl Electric Energy of Available Group |  | 0 |  |  | 1KWH
| 165 |  | 3 | Nomianl Electric Energy of On-grid Group |  | 0 |  |  | 1KWH
| 166 |  | 4 | Current Charging Energy(Kwh) of Stack |  | 0 |  |  | 1KWH
| 167 |  | 5 | Current Discharging Energy(Kwh) of Stack |  | 0 |  |  | 1KWH
| 168 | 72 | 0 | Continous Power-on Time of Stack System (High-order) |  | 0 | U16 |  | 1s
| 169 |  | 0 | Continous Power-on Time of Stack System (Low-order) |  | 0
| 170 |  | 1 | Available Charging Time of Stack (High-order) |  | 0
| 171 |  | 1 | Available Charging Time of Stack (Low-order) |  | 0 |  |  | 1min
| 172 |  | 2 | Available Discharging Time of Stack (High-order) |  | 0
| 173 |  | 2 | Available Discharging Time of Stack (Low-order) |  | 0 |  |  | 1min
| 174 | 73 | 0 | Inverter EmergentShutdown Message |  | 0 | U16 | 0,255 | 0xff: Emergent Stop 0x00: Normal
| 175 |  |  | Modbus Protocol Version |  | 103 | U16 | 103 Representing v001.03
BECU_0 | 180 | 80 | 0 | Voltage of Battery Group0 |  | 0 | U16 | [0,10000] | 0.1V | 1
| 181 |  | 1 | Current of Battery Group0 |  | 5000 |  | [0,10000] | Representing -5000—5000(0.1A)
| 182 |  | 2 | Current SOC of Battery Group0 |  | 0 |  | [0,10000] | 0.01%
| 183 |  | 3 | Overall Sampling Voltage of of Battery Group0 |  | 0 |  | [0,10000] | 0.1V
| 184 | 81 | 0 | SOH of Battery Group0 |  | 0 | U16 | [0,100] | %
| 185 |  | 1 | Battery Average Temperature of Battery Group0 |  | 40 |  | [0,200] | Representing -40-160℃
| 186 |  | 2 | Environmental Temperature of BatteryGroup0 |  | 40 |  | [0,200] | Representing-40-160℃ Representing -40-160℃
| 187 | 82 | 0 | Charging Current Limit Value of Battery Group0 |  | 0 | U16 | [0,5000] | 0.1A
| 188 |  | 1 | Discharging Current Limit Value of Battery Group0 |  | 0 |  | [0,5000] | 0.1A
| 189 | 90 | 0 | Remanet Energy of Battery Group0 (High-order) |  | 0 | U16 |  | 1wh
| 190 |  | 0 | Remanet Energy of Battery Group0 (Low-order) |  | 0
| 191 |  | 1 | Charing-discharging Times of Battery Group0 (High-order) |  | 0
| 192 |  | 1 | Charing-discharging Times of Battery Group0 (Low-order) |  | 0 |  |  | 1
| 193 |  | 2 | Overall Energy of Battery Group0(High-order) |  | 0 |  |  | 1wh
| 194 |  | 2 | Overall Energy of Battery Group0(Low-order) |  | 0
| 195 |  | 3 | Overall capacity of Battery Group0(High-order) |  | 0
| 196 |  | 3 | Overall capacity of Battery Group0(Low-order) |  | 0 |  |  | 1mAH
| 197 |  | 4 | Single Charing Energy of Battery Group0 (High-order) |  | 0 |  |  | 1wh
| 198 |  | 4 | Single Charing Energy of Battery Group0 (Low-order) |  | 0
| 199 |  | 5 | Single Discharing Energy of Battery Group0 (High-order) |  | 0
| 200 |  | 5 | Single Discharing Energy of Battery Group0 (Low-order) |  | 0 |  |  | 1wh
| 201 |  | 6 | Single Charing capacity of Battery Group0 (High-order) |  | 0 |  |  | 1MAH
| 202 |  | 6 | Single Charing capacity of Battery Group0 (Low-order) |  | 0
| 203 |  | 7 | Single Discharing capacity of Battery Group0 (High-order) |  | 0
| 204 |  | 7 | Single Discharing capacity of Battery Group0 (Low-order) |  | 0 |  |  | 1MAH
| 205 |  | 8 | Historical Charging Energy of Battery Group0 (High-order) |  | 0 |  |  | 1wH
| 206 |  | 8 | Historical Charging Energy of Battery Group0 (Low-order) |  | 0
| 207 |  | 9 | Historical Discharging Energy of Battery Group0 (High-order) |  | 0
| 208 |  | 9 | Historical Discharging Energy of Battery Group0 (Low-order) |  | 0 |  |  | 1wH
| 209 |  | 10 | Historical Charging capacity of Battery Group0 (High-order) |  | 0 |  |  | 1MAH
| 210 |  | 10 | Historical Charging capacity of Battery Group0 (Low-order) |  | 0
| 211 |  | 11 | Historical Discharging capacity of Battery Group0 (High-order) |  | 0
| 212 |  | 11 | Historical Discharging capacity of Battery Group0 (Low-order) |  | 0 |  |  | 1MAH
| 213 |  | 12 | Actual Capacity of Battery Group0 (High-order) |  | 0
| 214 |  | 12 | Actual Capacity of Battery Group0 (Low-order) |  | 0 |  |  | 1MAH | 0
| 215 | 81 | 3 | Enviroment Humidity of Battery Group0 |  | 0 | U16 | [0,100] | %
| 216 | 91 | 1 | SOC Actual SOC of Battery Group0 |  | 0 |  | [0,100] | %
| 217 | 100 | 0 | Max. Voltage Cell No. of Battery Group0 |  | 0 | U16 | [0,1000] | 1 | 1
| 218 |  | 1 | The Voltage of the Max. Voltage cell of Battery Group0 |  | 0 |  | [0,5000] | mV
| 219 |  | 2 | The temperature of the Max. Voltage Cell of Battery Group0 |  | 40 |  | [0,200] | Representing -40-160℃
| 220 |  | 3 | Min. Voltage Cell No. of Battery Group0 |  | 0 |  | [0,1000] | 1
| 221 |  | 4 | Min. Voltage of Min. Voltage cell of Battery Group |  | 0 |  | [0,5000] | mV
| 222 |  | 5 | The temperature of the Min.Voltage Battery of Battery Group0 |  | 40 |  | [0,200] | Representing -40-160℃
| 223 | 110 | 0 | Max. Temperature cell No. of Battery Group0 |  | 0 | U16 | [0,1000] | 1 | 1
| 224 |  | 1 | The temperature of Max. Temperature Cell of Battery Group0 |  | 40 |  | [0,200] | Representing -40-160℃
| 225 |  | 2 | The voltage of Max.Temperature Cell of Battery Group0 |  | 0 |  | [0,5000] | mV
| 226 |  | 3 | Min. Temperature cell No. of Battery Group0 |  | 0 |  | [0,1000] | 1
| 227 |  | 4 | The Temperature of Min. Temperature cell of Battery Group0 |  | 40 |  | [0,200] | Representing -40-160℃
| 228 |  | 5 | The voltage of the Min. Temperature cell of Battery Group0 |  | 0 |  | [0,5000] | mV
| 230 | 101 | 0 | Voltage of Cell 0 |  | 0 | U16 | [0,5000] | mV | 1
| 231 |  | 1 | Voltage of Cell 1 |  | 0 |  | [0,5000] | mV
| 232 |  | 2 | Voltage of Cell 2 |  | 0 |  | [0,5000] | mV
| 233 |  | 3 | Voltage of Cell 3 |  | 0 |  | [0,5000] | mV
| 234 |  | 4 | Voltage of Cell 4 |  | 0 |  | [0,5000] | mV
| 235 |  | 5 | Voltage of Cell 5 |  | 0 |  | [0,5000] | mV
| 236 |  | 6 | Voltage of Cell 6 |  | 0 |  | [0,5000] | mV
| 237 |  | 7 | Voltage of Cell 7 |  | 0 |  | [0,5000] | mV
| 238 |  | 8 | Voltage of Cell 8 |  | 0 |  | [0,5000] | mV
| 239 |  | 9 | Voltage of Cell 9 |  | 0 |  | [0,5000] | mV
| 240 |  | 10 | Voltage of Cell 10 |  | 0 |  | [0,5000] | mV
| 241 |  | 11 | Voltage of Cell 11 |  | 0 |  | [0,5000] | mV
| 242 |  | 12 | Voltage of Cell 12 |  | 0 |  | [0,5000] | mV
| 243 |  | 13 | Voltage of Cell 13 |  | 0 |  | [0,5000] | mV
| .. |  | 14 | .. |  | 0 |  | [0,5000] | mV
| 259 |  | 15 | Voltage of Cell 29 |  | 0 |  | [0,5000] | mV
| 260 | 111 | 0 | Temperature of Cell 0 |  | 0 | U16 | [0,200] | Representing -40-160℃ | 1
| 261 |  | 1 | Temperature of Cell 1 |  | 0 |  | [0,200] | Representing -40-160℃
| 262 |  | 2 | Temperature of Cell 2 |  | 0 |  | [0,200] | Representing -40-160℃
| 263 |  | 3 | Temperature of Cell 3 |  | 0 |  | [0,200] | Representing -40-160℃
| 264 |  | 4 | Temperature of Cell 4 |  | 0 |  | [0,200] | Representing -40-160℃
| 265 |  | 5 | Temperature of Cell 5 |  | 0 |  | [0,200] | Representing -40-160℃
| 266 |  | 6 | Temperature of Cell 6 |  | 0 |  | [0,200] | Representing -40-160℃
| 267 |  | 7 | Temperature of Cell 7 |  | 0 |  | [0,200] | Representing -40-160℃
| 268 |  | 8 | Temperature of Cell 8 |  | 0 |  | [0,200] | Representing -40-160℃
| 269 |  | 9 | Temperature of Cell 9 |  | 0 |  | [0,200] | Representing -40-160℃
| 270 |  | 10 | Temperature of Cell 10 |  | 0 |  | [0,200] | Representing -40-160℃
| 271 |  | 11 | Temperature of Cell 11 |  | 0 |  | [0,200] | Representing -40-160℃
| 272 |  | 12 | Temperature of Cell 12 |  | 0 |  | [0,200] | Representing -40-160℃
| 273 |  | 13 | Temperature of Cell 13 |  | 0 |  | [0,200] | Representing -40-160℃
| .. |  | 14 | … |  | 0 |  | [0,200] | Representing -40-160℃
| 289 |  | 15 | Temperature of Cell 29 |  | 0 |  | [0,200] | Representing -40-160℃
| 290-319 | 130 | 0 | Charging Equilibrium Status of Cell 0~Cell 29 in Battery Group0 |  | 0 | U16 | [0,1] | 0: Not Equilibrium 1: Charging Equilibrium | 0
| 320-349 | 131 | 0 | Discharging Equilibrium Status of Cell 0~Cell 29 in Battery Group0 |  | 0 |  | [0,1] | 0: Not Equilibrium 1: Charging Equilibrium
BECU_1 | 380-579 |  |  | BECU1 Corresponding Information of Group1 (same as BECU_0) |  |  | U16
BECU_2 | 580-849 |  |  | BECU2 Corresponding Information of Group2 (same as BECU_0)
BECU_3 | 780-979 |  |  | BECU3 Corresponding Information of Group3 (same as BECU_0)
PCS Summary | 1100 |  |  | Inverter Networking Mode |  | 0 | U16 |  | 0: DC-bus Single phase； 1: AC-bus Single phase； 2: DC-bus Split phase； 3: AC-bus Split phase； 4: DC-bus Three phase； 5: AC-bus Three phase； | 1
| 1101 |  |  | Inverter Active Power Sum |  | 0 |  |  | 1w
| 1102 |  |  | Inverter Reactive Power Sum |  | 0 |  |  | 1Var
| 1103 |  |  | Inverter Apparent Power Sum |  | 0 |  |  | 1VA
| 1104 |  |  | Inverter Output Current Sum |  | 0 |  |  | 0.1A
| 1105 |  |  | Inverter Accumulative Discharging energy (High-order) |  | 0 |  |  | 0.1kwh
| 1106 |  |  | Inverter Accumulative Discharging energy (Low-order) |  | 0 |  |  | 0.1kwh
| 1107 |  |  | Inverter Accumulative Charging energy (High-order) |  | 0 |  |  | 0.1kwh
| 1108 |  |  | Inverter Accumulative Charging energy (Low-order) |  | 0 |  |  | 0.1kwh
| 1109 |  |  | Grid Accumulative Electricity Sold (High-order) |  | 0 |  |  | 0.1kwh
| 1110 |  |  | Grid Accumulative Electricity Sold (Low-order) |  | 0 |  |  | 0.1kwh
| 1111 |  |  | Grid Accumulative Electricity Bought (High-order) |  | 0 |  |  | 0.1kwh
| 1112 |  |  | Grid Accumulative Electricity Bought (Low-order) |  | 0 |  |  | 0.1kwh
| 1113 |  |  | Accumulative Electricity Used by load(High-order) |  | 0 |  |  | 0.1kwh
| 1114 |  |  | Accumulative Electricity Used by Load (Low-order) |  | 0 |  |  | 0.1kwh
| 1115 |  |  | PV Electricity Self-consumption (High-order) |  | 0 |  |  | 0.1kwh
| 1116 |  |  | PV Electricity Quantity Self-consumption (Low-order) |  | 0 |  |  | 0.1kwh
| 1117 |  |  | Battery elcttricity charged from grid (High-order) |  | 0 |  |  | 0.1kwh
| 1118 |  |  | Battery elcttricity charged from grid (Low-order) |  | 0 |  |  | 0.1kwh
| 1119 |  |  | Photovoltaic Inverter Electricity Sold (High-order) |  | 0 |  |  | 0.1kwh(Only Available in DC System)
| 1120 |  |  | Photovoltaic Inverter Electricity Quantity Sold (Low-order) |  | 0 |  |  | 0.1kwh(Only Available in DC System)
PCS_1 | 1130 |  |  | Inverter1 Operation Status (A-phase,Split phase L1, or Single-phase) |  |  |  | [0,11] | 0: Not Working 1: Off-grid Matching Load 2: On-grid Full power Charging 3: On-grid Full power Discharging 4: Grid-tied Matching Load Charging 5：Grid-tied Matching Load Discharging 6: Grid-tied Limited Power Discharging (Over-frequency) 7: Grid-tied Limited Power Charging (Over-temperature) 8: Grid-tied Limited Power Discharging (Over-temperature) 9: Grid-tied Limited Power Charging (Battery Full) 10: Grid-tied Limited Power Discharging (Battery Empty) 11: UPS Emergent Power Supply( Inverter not Working and Grid Connecting with Load)
| 1131 |  |  | Inverter1 Output Current (A-phase, Split phase L1, or Single-phase) |  |  |  |  | 0.1A
| 1132 |  |  | Inverter1 Outuput Voltage(A-phase, Split L1, or Single-phase) |  |  |  |  | 0.1V
| 1133 |  |  | Inverter1 Active Power(A-phase, Split phase L1, or Single-phase) |  |  |  |  | 1w |  | Production AC Phase 1
| 1134 |  |  | Inverter1 Reactive Power (A-phase,Split phase L1, or Single-phase) |  |  |  |  | 1w
| 1135 |  |  | Inverter1 Apparent Power (A-phase, Split phase L1, or Single-phase) |  |  |  |  | 1w
| 1136 |  |  | Grid Phase1 Current (A-phase, Split phase L1, or Single-phase) |  |  |  |  | 0.1A
| 1137 |  |  | Grid Phase1 Voltage (A-phase, Split phase L1, or Single-phase) |  |  |  |  | 0.1V
| 1138 |  |  | Grid Phase1 Active Power (A-phase, Split phase L1, or Single-phase) |  |  |  |  | 1w |  | Sell to/ buy from grid Phase 2
| 1139 |  |  | Grid Phase1 Reactive Power(A-phase, Split phase L1, or Single-phase) |  |  |  |  | 1w
| 1140 |  |  | Grid Phase1 Apparent Power (A-phase, Split phase L1, or Single-phase) |  |  |  |  | 1w
| 1141 |  |  | Phase1 Load Active Power (A-phase, Split phase L1, or Single-phase) |  |  |  |  | 1w |  | Consumption Phase 1
| 1142 |  |  | Phase1 Load Reactive Power (A-phase, Split phase L1, or Single-phase) |  |  |  |  | 1w
| 1143 |  |  | Phase1 Load Apparent Power (A-phase, Split phase L1, or Single-phase) |  |  |  |  | 1w
| 1144 |  |  | Phase1 Photovoltaic Inverter Active Power (A-phase, Split phase L1, or Single-phase) |  |  |  |  | 1w (Only Available in AC System)
PCS_2 | 1160 |  |  | Inverter2 Operation Status (B-phase,Split phase L2, Single-phase Reserved) |  | 0 |  | [0,11] | 0: Not Working 1: Off-grid Matching Load 2: On-grid Full power Charging 3: On-grid Full power Discharging 4: Grid-tied Matching Load Charging 5：Grid-tied Matching Load Discharging 6: Grid-tied Limited Power Discharging (Over-frequency) 7: Grid-tied Limited Power Charging (Over-temperature) 8: Grid-tied Limited Power Discharging (Over-temperature) 9: Grid-tied Limited Power Charging (Battery Full) 10: Grid-tied Limited Power Discharging (Battery Empty) 11: UPS Emergent Power Supply( Inverter not Working and Grid Connecting with Load)
| 1161 |  |  | Inverter2 Output Current (B-phase, Split Phase L2, Single-phase Reserved) |  |  |  |  | 0.1A
| 1162 |  |  | Inverter2 Output Voltage(B-phase, Split Phase L2, Single-phase Reserved) |  |  |  |  | 0.1V
| 1163 |  |  | Inverter2 Active Power (B-phase, Split Phase L2, Single-phase Reserved) |  |  |  |  | 1w |  | Production AC Phase 2
| 1164 |  |  | Inverter2 Reactive Power (B-phase, Split Phase L2, Single-phase Reserved) |  |  |  |  | 1w
| 1165 |  |  | Inverter2 Apparent Power (B-phase, Split Phase L2, Single-phase Reserved) |  |  |  |  | 1w
| 1166 |  |  | Grid Phase2 Current(B-phase,Split Phase L2, Single-phase Reserved) |  |  |  |  | 0.1A
| 1167 |  |  | Grid Phase2 Voltage (B-phase, Split Phase L2, Single-phase Reserved) |  |  |  |  | 0.1V
| 1168 |  |  | Grid Phase2 Active Power (B-phase, Split Phase L2, Single-phase Reserved) |  |  |  |  | 1w |  | Sell to/ buy from grid Phase 2
| 1169 |  |  | Grid Phase2 Reactive Power (B-phase, Split Phase L2, Single-phase Reserved) |  |  |  |  | 1w
| 1170 |  |  | Grid Phase2 Apparent Power (B-phase, Split Phase L2, Single-phase Reserved) |  |  |  |  | 1w
| 1171 |  |  | Phase2 Load Actvive Power (B-phase, Split Phase L2, Single-phase Reserved) |  |  |  |  | 1w |  | Consumption Phase 2
| 1172 |  |  | Phase2 Load Reactive Power (B-phase, Split Phase L2, Single-phase Reserved) |  |  |  |  | 1w
| 1173 |  |  | Phase2 Load Apparent Power (B-phase, Split Phase L2, Single-phase Reserved) |  |  |  |  | 1w
| 1174 |  |  | Phase2 Photovoltaic Inverter Active Power (B-phase, Split Phase L2, Single-phase Reserved) |  |  |  |  | 1w (Only Available in AC System)
PCS_3 | 1190 |  |  | Inverter3 Operation Status (C-phase, Split phase & Single-phase Reserved) |  |  |  | [0,11] | 0: Not Working 1: Off-grid Matching Load 2: On-grid Full power Charging 3: On-grid Full power Discharging 4: Grid-tied Matching Load Charging 5：Grid-tied Matching Load Discharging 6: Grid-tied Limited Power Discharging (Over-frequency) 7: Grid-tied Limited Power Charging (Over-temperature) 8: Grid-tied Limited Power Discharging (Over-temperature) 9: Grid-tied Limited Power Charging (Battery Full) 10: Grid-tied Limited Power Discharging (Battery Empty) 11: UPS Emergent Power Supply( Inverter not Working and Grid Connecting with Load)
| 1191 |  |  | Inverter3 Output Current (C-phase, Split phase & Single-phase Reserved) |  |  |  |  | 0.1A
| 1192 |  |  | Inverter3 Outuput Voltage (C-phase, Split phase & Single-phase Reserved) |  |  |  |  | 0.1V
| 1193 |  |  | Inverter3 Active Power (C-phase, Split phase & Single-phase Reserved) |  |  |  |  | 1w |  | Production AC Phase 3
| 1194 |  |  | Inverter3 Reactive Power (C-phase, Split phase & Single-phase Reserved) |  |  |  |  | 1w
| 1195 |  |  | Inverter3 Apparent Power (C-phase, Split phase & Single-phase Reserved) |  |  |  |  | 1w
| 1196 |  |  | Grid Phase3 Current (C-phase, Split phase & Single-phase Reserved) |  |  |  |  | 0.1A
| 1197 |  |  | Grid Phase3 Voltage (C-phase, Split phase & Single-phase Reserved) |  |  |  |  | 0.1V
| 1198 |  |  | Grid Phase3 Active Power (C-phase, Split phase & Single-phase Reserved) |  |  |  |  | 1w |  | Sell to/ buy from grid Phase 3
| 1199 |  |  | Grid Phase3 Reactive Power (C-phase, Split phase & Single-phase Reserved) |  |  |  |  | 1w
| 1200 |  |  | Grid Phase3 Apparent Power (C-phase, Split phase & Single-phase Reserved) |  |  |  |  | 1w
| 1201 |  |  | Grid Phase3 Load Active Power (C-phase, Split phase & Single-phase Reserved) |  |  |  |  | 1w |  | Consumption Phase 3
| 1202 |  |  | Grid Phase3 Load Reactvie Power (C-phase, Split phase & Single-phase Reserved) |  |  |  |  | 1w
| 1203 |  |  | Phase 3 Load Apparent Power (C-phase, Split phase & Single-phase Reserved) |  |  |  |  | 1w
| 1204 |  |  | Phase 3 Photovoltaic Inverter Active Power (C-phase, Split phase & Single-phase Reserved) |  |  |  |  | 1w (Only Available in AC System)
PV Summary | 1220 |  |  | Number of Charger |  | 0 | U16 |  | pcs (Only Available in DC System) | 1
| 1221 |  |  | Charger Total Output Current |  | 0 |  |  | 0.1A (Only Available in DC System)
| 1222 |  |  | Charger Total Output Power |  | 0 |  |  | 1w (Only Available in DC System)
| 1223 |  |  | Charger Cumulatvie Ouput (High-order) |  | 0
| 1224 |  |  | Charger Cumulatvie Ouput (Low-order) |  | 0 |  |  | 1kwh (Only Available in DC System)
PV_1 | 1230 |  |  | Charger 1 Output Voltage |  | 0 |  |  | 0.1V (Only Available in DC System) | 1
| 1231 |  |  | Charger 1 Output Current |  | 0 |  |  | 0.1A (Only Available in DC System)
| 1232 |  |  | Charger 1 Output Power |  | 0 |  |  | 1w (Only Available in DC System) |  | Production PV 1
| 1233 |  |  | Charger 1 Output Voltage |  | 0 |  |  | 0.1V (Only Available in DC System)
| 1234 |  |  | Charger 1 Radiator Temperature |  | 0 |  |  | 1℃(Only Available in DC System)
| 1235 |  |  | Charger 1 Cumulative Output (High-order) |  | 0
| 1236 |  |  | Charger 1 Cumulative Output (Low-order) |  | 0 |  |  | 1kwh (Only Available in DC System)
PV_2 | 1240 |  |  | Charger 2 Output Voltage |  | 0 |  |  | 0.1V (Only Available in DC System) | 1
| 1241 |  |  | Charger 2 Output Current |  | 0 |  |  | 0.1A (Only Available in DC System)
| 1242 |  |  | Charger 2 Output Power |  | 0 |  |  | 1w (Only Available in DC System) |  | Production PV 2
| 1243 |  |  | Charger 2 Output Voltage |  | 0 |  |  | 0.1V (Only Available in DC System)
| 1244 |  |  | Charger 2 Radiator Temperature |  | 0 |  |  | 1℃(Only Available in DC System)
| 1245 |  |  | Charger 2 Cumulative Output(High-order) |  | 0
| 1246 |  |  | Charger 1 Cumulative Output (Low-order) |  | 0 |  |  | 1kwh (Only Available in DC System)
Remote control | 2988 |  |  | Active Power |  | 0 | S16 | [0,9000] [56536,65535] | 0-9000 Representing 0 to +9000W，0,+3000W each pahse,65535-56536 Representing -1W to -9000W，-1W to -3000W each phase,plus Representing discharge, minus Representing charge | 1
| 2989 |  |  | Reactive Power |  | 0 | S16 | [0,9000] [56536,65535] | 0-9000 Representing 0 to +9000W，0,+3000W each pahse,65535-56536 Representing -1W to -9000W，-1W to -3000W each phase,plus Representing discharge, minus Representing charge | 1
| 2990 |  |  | Power adjustment |  | 0 | U16 | 0, 1,2 | 0: Local Control 1: Accept remote control, Active pover base on active power value, Reactive power base on power factor 2: Accept remote control, Active pover base on active power value, Reactive power base on reactive power value | 1
| 2991 |  |  | Power factor |  | 1000 | U16 | [900，1000] [1001,1100] | 900 to 1000, representing 0.900 to -0.900 100 to 1100, representing -0.999 to 1.00; | 1

## Fault List
Stack Fault Information 0
No. | Definition | Value/Status |  | Inverter Fault Inforamtion 1
0 | No Enabling Group or no Availabel Battery Group | 0: Normal 1: Fault | new BitItemOnOff(0, "No Enabling Group or no Availabel Battery Group"), | No. | Definition | Value/Status
1 | Stack Common Leakage | 0: Normal 1: Fault | new BitItemOnOff(1, "Stack Common Leakage"), | 0 | Over-load (100%-110%) | 0: Normal 1: Fault | new BitItemOnOff(0, "Over-load (100%-110%)"),
2 | Stack Serious Leakage | 0: Normal 1: Fault | new BitItemOnOff(2, "Stack Serious Leakage"), | 1 | Over-load (110%-120%) | 0: Normal 1: Fault | new BitItemOnOff(1, "Over-load (110%-120%)"),
3 | Stack Startup Failed | 0: Normal 1: Fault | new BitItemOnOff(3, "Stack Startup Failed"), | 2 | Over-load (120-150%) | 0: Normal 1: Fault | new BitItemOnOff(2, "Over-load (120-150%)"),
4 | Stack Shutdown Failed | 0: Normal 1: Fault | new BitItemOnOff(4, "Stack Shutdown Failed"), | 3 | Over-load (150%-200%) | 0: Normal 1: Fault | new BitItemOnOff(3, "Over-load (150%-200%)"),
5 | Reserved | 0: Normal 1: Fault | new BitItemOnOff(5, "Reserved"), | 4 | Over-load (200%-220%) | 0: Normal 1: Fault | new BitItemOnOff(4, "Over-load (200%-220%)"),
6 | Reserved | 0: Normal 1: Fault | new BitItemOnOff(6, "Reserved"), | 5 | Over-load (220%-300%) | 0: Normal 1: Fault | new BitItemOnOff(5, "Over-load (220%-300%)"),
7 | Reserved | 0: Normal 1: Fault | new BitItemOnOff(7, "Reserved"), | 6 | Inveter serious Over-Current | 0: Normal 1: Fault | new BitItemOnOff(6, "Inveter serious Over-Current"),
8 | Reserved | 0: Normal 1: Fault | new BitItemOnOff(8, "Reserved"), | 7 | Grid Over-Current | 0: Normal 1: Fault | new BitItemOnOff(7, "Grid Over-Current"),
9 | Reserved | 0: Normal 1: Fault | new BitItemOnOff(9, "Reserved"), | 8 | Repeatly Inverter common over-currents | 0: Normal 1: Fault | new BitItemOnOff(8, "Repeatly Inverter common over-currents"),
10 | Reserved | 0: Normal 1: Fault | new BitItemOnOff(10, "Reserved"), | 9 | Invert voltage sampling ref. error | 0: Normal 1: Fault | new BitItemOnOff(9, "Invert voltage sampling ref. error"),
11 | Reserved | 0: Normal 1: Fault | new BitItemOnOff(11, "Reserved"), | 10 | Grid voltage sampling ref. error | 0: Normal 1: Fault | new BitItemOnOff(10, "Grid voltage sampling ref. error"),
12 | Reserved | 0: Normal 1: Fault | new BitItemOnOff(12, "Reserved"), | 11 | Control Current sampling ref. error | 0: Normal 1: Fault | new BitItemOnOff(11, "Control Current sampling ref. error"),
13 | Reserved | 0: Normal 1: Fault | new BitItemOnOff(13, "Reserved"), | 12 | Invert Current sampling ref. error | 0: Normal 1: Fault | new BitItemOnOff(12, "Invert Current sampling ref. error"),
14 | Reserved | 0: Normal 1: Fault | new BitItemOnOff(14, "Reserved"), | 13 | Grid Current sampling ref. error | 0: Normal 1: Fault | new BitItemOnOff(13, "Grid Current sampling ref. error"),
15 | Reserved | 0: Normal 1: Fault | new BitItemOnOff(15, "Reserved"), | 14 | PDP Protection (Power Components Driver Protection) | 0: Normal 1: Fault | new BitItemOnOff(14, "PDP Protection (Power Components Driver Protection)"),
Stack Fault Information 1 |  |  |  | 15 | Hardware over-current protection | 0: Normal 1: Fault | new BitItemOnOff(15, "Hardware over-current protection"),
No. | Definition | Value/Status |  | Inverter Fault Inforamtion 2
0 | CAN Communication between Stack and Group 0 broken | 0: Normal 1: Fault | new BitItemOnOff(0, "CAN Communication between Stack and Group 0 broken"), | No. | Definition | Value/Status
1 | CAN Communication between Stack and Group 1 broken | 0: Normal 1: Fault | new BitItemOnOff(1, "CAN Communication between Stack and Group 1 broken"), | 0 | Hardware Invert Over-Voltage Protection | 0: Normal 1: Fault | new BitItemOnOff(0, "Hardware Invert Over-Voltage Protection"),
2 | CAN Communication between Stack and Group 2 broken | 0: Normal 1: Fault | new BitItemOnOff(2, "CAN Communication between Stack and Group 2 broken"), | 1 | Hardware DC Over-Voltage Protection | 0: Normal 1: Fault | new BitItemOnOff(1, "Hardware DC Over-Voltage Protection"),
3 | CAN Communication between Stack and Group 3 broken | 0: Normal 1: Fault | new BitItemOnOff(3, "CAN Communication between Stack and Group 3 broken"), | 2 | Hardware Over-Temperature Protection | 0: Normal 1: Fault | new BitItemOnOff(2, "Hardware Over-Temperature Protection"),
4 | CAN Communication between Stack and Group 4 broken | 0: Normal 1: Fault | new BitItemOnOff(4, "CAN Communication between Stack and Group 4 broken"), | 3 | No Signal Captured | 0: Normal 1: Fault | new BitItemOnOff(3, "No Signal Captured"),
5 | CAN Communication between Stack and Group 5 broken | 0: Normal 1: Fault | new BitItemOnOff(5, "CAN Communication between Stack and Group 5 broken"), | 4 | DC Over-Voltage | 0: Normal 1: Fault | new BitItemOnOff(4, "DC Over-Voltage"),
6 | CAN Communication between Stack and Group 6 broken | 0: Normal 1: Fault | new BitItemOnOff(6, "CAN Communication between Stack and Group 6 broken"), | 5 | Battery disconnected | 0: Normal 1: Fault | new BitItemOnOff(5, "Battery disconnected"),
7 | CAN Communication between Stack and Group 7 broken | 0: Normal 1: Fault | new BitItemOnOff(7, "CAN Communication between Stack and Group 7 broken"), | 6 | Invert under-Voltage | 0: Normal 1: Fault | new BitItemOnOff(6, "Invert under-Voltage"),
8 | CAN Communication between Stack and Group 8 broken | 0: Normal 1: Fault | new BitItemOnOff(8, "CAN Communication between Stack and Group 8 broken"), | 7 | Invert Over-Voltage | 0: Normal 1: Fault | new BitItemOnOff(7, "Invert Over-Voltage"),
9 | CAN Communication between Stack and Group 9 broken | 0: Normal 1: Fault | new BitItemOnOff(9, "CAN Communication between Stack and Group 9 broken"), | 8 | Current Sensor Fault | 0: Normal 1: Fault | new BitItemOnOff(8, "Current Sensor Fault"),
10 | CAN Communication between Stack and Group 10 broken | 0: Normal 1: Fault | new BitItemOnOff(10, "CAN Communication between Stack and Group 10 broken"), | 9 | Voltage Sensor Fault | 0: Normal 1: Fault | new BitItemOnOff(9, "Voltage Sensor Fault"),
11 | CAN Communication between Stack and Group 11 broken | 0: Normal 1: Fault | new BitItemOnOff(11, "CAN Communication between Stack and Group 11 broken"), | 10 | Reserved | 0: Normal 1: Fault | new BitItemOnOff(10, "Reserved"),
12 | CAN Communication between Stack and Group 12 broken | 0: Normal 1: Fault | new BitItemOnOff(12, "CAN Communication between Stack and Group 12 broken"), | 11 | Reserved | 0: Normal 1: Fault | new BitItemOnOff(11, "Reserved"),
13 | CAN Communication between Stack and Group 13 broken | 0: Normal 1: Fault | new BitItemOnOff(13, "CAN Communication between Stack and Group 13 broken"), | 12 | Fan Fault | 0: Normal 1: Fault | new BitItemOnOff(12, "Fan Fault"),
14 | CAN Communication between Stack and Group 14 broken | 0: Normal 1: Fault | new BitItemOnOff(14, "CAN Communication between Stack and Group 14 broken"), | 13 | Phase break | 0: Normal 1: Fault | new BitItemOnOff(13, "Phase break"),
15 | CAN Communication between Stack and Group 15 broken | 0: Normal 1: Fault | new BitItemOnOff(15, "CAN Communication between Stack and Group 15 broken"), | 14 | Invert Relay Fault | 0: Normal 1: Fault | new BitItemOnOff(14, "Invert Relay Fault"),
|  |  |  | 15 | Grid Relay Fault | 0: Normal 1: Fault | new BitItemOnOff(15, "Grid Relay Fault"),
Group 0 Fault Information 0 |  |  |  | Inverter Fault Inforamtion 3
No. | Definition | Value/Status |  | No. | Definition | Value/Status
0 | Reserved | 0: Normal 1: Fault |  | 0 | Control PCB Over-temperature | 0: Normal 1: Fault | new BitItemOnOff(0, "Control PCB Over-temperature"),
1 | Reserved | 0: Normal 1: Fault |  | 1 | Power PCB Over-temperature | 0: Normal 1: Fault | new BitItemOnOff(1, "Power PCB Over-temperature"),
2 | Voltage sampling Circuit abnormal | 0: Normal 1: Fault |  | 2 | DC terminal Over-temperature | 0: Normal 1: Fault | new BitItemOnOff(2, "DC terminal Over-temperature"),
3 | Reserved | 0: Normal 1: Fault |  | 3 | Capacitor Over-temperature | 0: Normal 1: Fault | new BitItemOnOff(3, "Capacitor Over-temperature"),
4 | Voltage Sampling Circuit Disconnected | 0: Normal 1: Fault |  | 4 | Radiator Over-temperature | 0: Normal 1: Fault | new BitItemOnOff(4, "Radiator Over-temperature"),
5 | Temperature Sampling Circuit Disconnected | 0: Normal 1: Fault |  | 5 | Transformer Over-temperature | 0: Normal 1: Fault | new BitItemOnOff(5, "Transformer Over-temperature"),
6 | Main CAN and Sub CAN Disconnected (CAN in BMS Broken) | 0: Normal 1: Fault |  | 6 | 3-phase Combine Communication Fault | 0: Normal 1: Fault | new BitItemOnOff(6, "3-phase Combine Communication Fault"),
7 | Reserved | 0: Normal 1: Fault |  | 7 | EEPROM Fault | 0: Normal 1: Fault | new BitItemOnOff(7, "EEPROM Fault"),
8 | Reserved | 0: Normal 1: Fault |  | 8 | Load sampling ref. error | 0: Normal 1: Fault | new BitItemOnOff(8, "Load sampling ref. error"),
9 | Current Sampling Failure | 0: Normal 1: Fault |  | 9 | Power on current limitation fault | 0: Normal 1: Fault | new BitItemOnOff(9, "Power on current limitation fault"),
10 | Battery Failure | 0: Normal 1: Fault |  | 10 | 3-phase Combine Singal Synchronization Mistake | 0: Normal 1: Fault | new BitItemOnOff(10, "3-phase Combine Singal Synchronization Mistake"),
11 | Contactor 1 Abnormal | 0: Normal 1: Fault |  | 11 | Reserved | 0: Normal 1: Fault | new BitItemOnOff(11, "Reserved"),
12 | Contactor 2 Abnormal | 0: Normal 1: Fault |  | 12 | Reserved | 0: Normal 1: Fault | new BitItemOnOff(12, "Reserved"),
13 | Contactor 3 Abnormal | 0: Normal 1: Fault |  | 13 | Reserved | 0: Normal 1: Fault | new BitItemOnOff(13, "Reserved"),
14 | Contactor 4 Abnormal | 0: Normal 1: Fault |  | 14 | Reserved | 0: Normal 1: Fault | new BitItemOnOff(14, "Reserved"),
15 | Contactor 5 Abnormal | 0: Normal 1: Fault |  | 15 | Reserved | 0: Normal 1: Fault | new BitItemOnOff(15, "Reserved"),
Gropu0 Fault Information 1
No. | Definition | Value/Status |  | Charger Fault Inforamtion
0 | Reserved | 0: Normal 1: Fault |  | No. | Definition | Value/Status
1 | Reserved | 0: Normal 1: Fault |  | 0 | IPM Protection | 0: Normal 1: Fault | new BitItemOnOff(0, "IPM Protection"),
2 | Serious High-temperature Fault | 0: Normal 1: Fault |  | 1 | A-circuit Over-Current | 0: Normal 1: Fault | new BitItemOnOff(1, "A-circuit Over-Current"),
3 | Reserved | 0: Normal 1: Fault |  | 2 | B-circuit Over-Current | 0: Normal 1: Fault | new BitItemOnOff(2, "B-circuit Over-Current"),
4 | Reserved | 0: Normal 1: Fault |  | 3 | PV Over-Voltage | 0: Normal 1: Fault | new BitItemOnOff(3, "PV Over-Voltage"),
5 | Reserved | 0: Normal 1: Fault |  | 4 | Current Sensor Failure | 0: Normal 1: Fault | new BitItemOnOff(4, "Current Sensor Failure"),
6 | Reserved | 0: Normal 1: Fault |  | 5 | Radiator Over-temperature | 0: Normal 1: Fault | new BitItemOnOff(5, "Radiator Over-temperature"),
7 | Smoke Warning | 0: Normal 1: Fault |  | 6 | Relay Failure | 0: Normal 1: Fault | new BitItemOnOff(6, "Relay Failure"),
8 | Fuse Protector Over-temperature Fault | 0: Normal 1: Fault |  | 7 | Battery Voltage Sampling Failure | 0: Normal 1: Fault | new BitItemOnOff(7, "Battery Voltage Sampling Failure"),
9 | Rre-reserved | 0: Normal 1: Fault |  | 8 | Reserved | 0: Normal 1: Fault | new BitItemOnOff(8, "Reserved"),
10 | Common Leakage | 0: Normal 1: Fault |  | 9 | Reserved | 0: Normal 1: Fault | new BitItemOnOff(9, "Reserved"),
11 | Serious Leakage | 0: Normal 1: Fault |  | 10 | Reserved | 0: Normal 1: Fault | new BitItemOnOff(10, "Reserved"),
12 | Main CAN and Stack CAN Disconnected (CAN Outside BMS Disconnected） | 0: Normal 1: Fault |  | 11 | Reserved | 0: Normal 1: Fault | new BitItemOnOff(11, "Reserved"),
13 | Negtive Contactor open | 0: Normal 1: Fault |  | 12 | Reserved | 0: Normal 1: Fault | new BitItemOnOff(12, "Reserved"),
14 | Reserved | 0: Normal 1: Fault |  | 13 | Reserved | 0: Normal 1: Fault | new BitItemOnOff(13, "Reserved"),
15 | Reserved | 0: Normal 1: Fault |  | 14 | Reserved | 0: Normal 1: Fault | new BitItemOnOff(14, "Reserved"),
NOTE: the fault information of other groups is the same with Group 0 |  |  |  | 15 | Reserved | 0: Normal 1: Fault | new BitItemOnOff(15, "Reserved"),
Stack Fault Information 2
No. | Definition | Value/Status |  | Group 2 Fault Information 0
0 | Group 0 Main Contactor Abnormal | 0: Normal 1: Fault |  | No. | Definition | Value/Status
1 | Group 1 Main Contactor Abnormal | 0: Normal 1: Fault |  | 0 | Group 2 Reserved | 0: Normal 1: Fault
2 | Group 2 Main Contactor Abnormal | 0: Normal 1: Fault |  | 1 | Group 2 Reserved | 0: Normal 1: Fault
3 | Group 3 Main Contactor Abnormal | 0: Normal 1: Fault |  | 2 | Group 2 Voltage Sampling Circuit Abnormal | 0: Normal 1: Fault
4 | Group 4 Main Contactor Abnormal | 0: Normal 1: Fault |  | 3 | Group 2 Reserved | 0: Normal 1: Fault
5 | Group 5 Main Contactor Abnormal | 0: Normal 1: Fault |  | 4 | Group 2 Voltage Sampling Circuit Disconnected | 0: Normal 1: Fault
6 | Group 6 Main Contactor Abnormal | 0: Normal 1: Fault |  | 5 | Group 2 Temperature Sampling Circuit Disconnected | 0: Normal 1: Fault
7 | Group 7 Main Contactor Abnormal | 0: Normal 1: Fault |  | 6 | Group 2 Main-sub Interior CAN Disconnected | 0: Normal 1: Fault
8 | Group 8 Main Contactor Abnormal | 0: Normal 1: Fault |  | 7 | Group 2 Reserved | 0: Normal 1: Fault
9 | Group 9 Main Contactor Abnormal | 0: Normal 1: Fault |  | 8 | Group 2 Reserved | 0: Normal 1: Fault
10 | Group 10 Main Contactor Abnormal | 0: Normal 1: Fault |  | 9 | Group 2 Current Sampling Circuit Failure | 0: Normal 1: Fault
11 | Group 11 Main Contactor Abnormal | 0: Normal 1: Fault |  | 10 | Group 2 Battery Cell Failure | 0: Normal 1: Fault
12 | Group 12 Main Contactor Abnormal | 0: Normal 1: Fault |  | 11 | Group 2 main contactor abnormal | 0: Normal 1: Fault
13 | Group 13 Main Contactor Abnormal | 0: Normal 1: Fault |  | 12 | Group 2 Pre-charging contactor abnormal | 0: Normal 1: Fault
14 | Group 14 Main Contactor Abnormal | 0: Normal 1: Fault |  | 13 | Group 2 Reserved | 0: Normal 1: Fault
15 | Group 15 Main Contactor Abnormal | 0: Normal 1: Fault |  | 14 | Group 2 BMU Power contactor abnormal | 0: Normal 1: Fault
Stack Fault Information 3 |  |  |  | 15 | Group 2 Reserved | 0: Normal 1: Fault
No. | Definition | Value/Status |  | Group 2 Fault Information 1
0 | Group 0 precharging Contactor Abnormal | 0: Normal 1: Fault |  | No. | Definition | Value/Status
1 | Group 1 precharging Contactor Abnormal | 0: Normal 1: Fault |  | 0 | Group 2 Reserved | 0: Normal 1: Fault
2 | Group 2 precharging Contactor Abnormal | 0: Normal 1: Fault |  | 1 | Group 2 Reserved | 0: Normal 1: Fault
3 | Group 3 precharging Contactor Abnormal | 0: Normal 1: Fault |  | 2 | Group 2 Serious High-temperature Failure | 0: Normal 1: Fault
4 | Group 4 precharging Contactor Abnormal | 0: Normal 1: Fault |  | 3 | Group 2 Reserved | 0: Normal 1: Fault
5 | Group 5 precharging Contactor Abnormal | 0: Normal 1: Fault |  | 4 | Group 2 Reserved | 0: Normal 1: Fault
6 | Group 6 precharging Contactor Abnormal | 0: Normal 1: Fault |  | 5 | Group 2 Reserved | 0: Normal 1: Fault
7 | Group 7 precharging Contactor Abnormal | 0: Normal 1: Fault |  | 6 | Group 2 Reserved | 0: Normal 1: Fault
8 | Group 8 precharging Contactor Abnormal | 0: Normal 1: Fault |  | 7 | Group 2 Reserved | 0: Normal 1: Fault
9 | Group 9 precharging Contactor Abnormal | 0: Normal 1: Fault |  | 8 | Group 2 Fuse Failure | 0: Normal 1: Fault
10 | Group 10 precharging Contactor Abnormal | 0: Normal 1: Fault |  | 9 | Group 2 Reserved | 0: Normal 1: Fault
11 | Group 11 precharging Contactor Abnormal | 0: Normal 1: Fault |  | 10 | Group 2 Reserved | 0: Normal 1: Fault
12 | Group 12 precharging Contactor Abnormal | 0: Normal 1: Fault |  | 11 | Group 2 Reserved | 0: Normal 1: Fault
13 | Group 13 precharging Contactor Abnormal | 0: Normal 1: Fault |  | 12 | Group 2 Disconnected with Stack Communication CAN | 0: Normal 1: Fault
14 | Group 14 precharging Contactor Abnormal | 0: Normal 1: Fault |  | 13 | Group 2 Reserved | 0: Normal 1: Fault
15 | Group 15 precharging Contactor Abnormal | 0: Normal 1: Fault |  | 14 | Group 2 BMU Power Contactor Disconnected | 0: Normal 1: Fault
Stack Fault Information 4 |  |  |  | 15 | Group 2 Reserved | 0: Normal 1: Fault
No. | Definition | Value/Status |  | Group 3 Fault Information 0
0 | Group 0 Main Contactor Failure | 0: Normal 1: Fault |  | No. | Definition | Value/Status
1 | Group 1 Main Contactor Failure | 0: Normal 1: Fault |  | 0 | Group 3 Reserved | 0: Normal 1: Fault
2 | Group 2 Main Contactor Failure | 0: Normal 1: Fault |  | 1 | Group 3 Reserved | 0: Normal 1: Fault
3 | Group 3 Main Contactor Failure | 0: Normal 1: Fault |  | 2 | Group 3 Voltage Sampling Circuit Abnormal | 0: Normal 1: Fault
4 | Group 4 Main Contactor Failure | 0: Normal 1: Fault |  | 3 | Group 3 Reserved | 0: Normal 1: Fault
5 | Group 5 Main Contactor Failure | 0: Normal 1: Fault |  | 4 | Group 3 Voltage Sampling Circuit Disconnected | 0: Normal 1: Fault
6 | Group 6 Main Contactor Failure | 0: Normal 1: Fault |  | 5 | Group 3 Temperature Sampling Circuit Disconnected | 0: Normal 1: Fault
7 | Group 7 Main Contactor Failure | 0: Normal 1: Fault |  | 6 | Group 3 Main-sub Interior CAN Disconnected | 0: Normal 1: Fault
8 | Group 8 Main Contactor Failure | 0: Normal 1: Fault |  | 7 | Group 3 Reserved | 0: Normal 1: Fault
9 | Group 9 Main Contactor Failure | 0: Normal 1: Fault |  | 8 | Group 3 Reserved | 0: Normal 1: Fault
10 | Group 10 Main Contactor Failure | 0: Normal 1: Fault |  | 9 | Group 3 Current Sampling Circuit Failure | 0: Normal 1: Fault
11 | Group 11 Main Contactor Failure | 0: Normal 1: Fault |  | 10 | Group 3 Battery Cell Failure | 0: Normal 1: Fault
12 | Group 12 Main Contactor Failure | 0: Normal 1: Fault |  | 11 | Group 3 main contactor abnormal | 0: Normal 1: Fault
13 | Group 13 Main Contactor Failure | 0: Normal 1: Fault |  | 12 | Group 3 Pre-charging contactor abnormal | 0: Normal 1: Fault
14 | Group 14 Main Contactor Failure | 0: Normal 1: Fault |  | 13 | Group 3 Reserved | 0: Normal 1: Fault
15 | Group 15 Main Contactor Failure | 0: Normal 1: Fault |  | 14 | Group 3 BMU Power contactor abnormal | 0: Normal 1: Fault
Stack Fault Information 5 |  |  |  | 15 | Group 3 Reserved | 0: Normal 1: Fault
No. | Definition | Value/Status |  | Group 3 Fault Information 1
0 | Group 0 Precharging Contactor Failure | 0: Normal 1: Fault |  | No. | Definition | Value/Status
1 | Group 1 Precharging Contactor Failure | 0: Normal 1: Fault |  | 0 | Group 3 Reserved | 0: Normal 1: Fault
2 | Group 2 Precharging Contactor Failure | 0: Normal 1: Fault |  | 1 | Group 3 Reserved | 0: Normal 1: Fault
3 | Group 3 Precharging Contactor Failure | 0: Normal 1: Fault |  | 2 | Group 3 Serious High-temperature Failure | 0: Normal 1: Fault
4 | Group 4 Precharging Contactor Failure | 0: Normal 1: Fault |  | 3 | Group 3 Reserved | 0: Normal 1: Fault
5 | Group 5 Precharging Contactor Failure | 0: Normal 1: Fault |  | 4 | Group 3 Reserved | 0: Normal 1: Fault
6 | Group 6 Precharging Contactor Failure | 0: Normal 1: Fault |  | 5 | Group 3 Reserved | 0: Normal 1: Fault
7 | Group 7 Precharging Contactor Failure | 0: Normal 1: Fault |  | 6 | Group 3 Reserved | 0: Normal 1: Fault
8 | Group 8 Precharging Contactor Failure | 0: Normal 1: Fault |  | 7 | Group 3 Reserved | 0: Normal 1: Fault
9 | Group 9 Precharging Contactor Failure | 0: Normal 1: Fault |  | 8 | Group 3 Fuse Protector Failure | 0: Normal 1: Fault
10 | Group 10 Precharging Contactor Failure | 0: Normal 1: Fault |  | 9 | Group 3 Reserved | 0: Normal 1: Fault
11 | Group 11 Precharging Contactor Failure | 0: Normal 1: Fault |  | 10 | Group 3 Reserved | 0: Normal 1: Fault
12 | Group 12 Precharging Contactor Failure | 0: Normal 1: Fault |  | 11 | Group 3 Reserved | 0: Normal 1: Fault
13 | Group 13 Precharging Contactor Failure | 0: Normal 1: Fault |  | 12 | Group 3 Disconnected with Stack Communication CAN | 0: Normal 1: Fault
14 | Group 14 Precharging Contactor Failure | 0: Normal 1: Fault |  | 13 | Group 3 Reserved | 0: Normal 1: Fault
15 | Group 15 Precharging Contactor Failure | 0: Normal 1: Fault |  | 14 | Group 3 BMU Power Contactor Disconnected | 0: Normal 1: Fault
|  |  |  | 15 | Group 3 Reserved | 0: Normal 1: Fault
Group 1 Fault Information 0 |  |  |  | Group 4 Fault Information 0
No. | Definition | Value/Status |  | No. | Definition | Value/Status
0 | Group 1 Reserved | 0: Normal 1: Fault |  | 0 | Group 4 Reserved | 0: Normal 1: Fault
1 | Group 1 Reserved | 0: Normal 1: Fault |  | 1 | Group 4 Reserved | 0: Normal 1: Fault
2 | Group 1 Voltage Sampling Circuit Abnormal | 0: Normal 1: Fault |  | 2 | Group 4 Voltage Sampling Circuit Abnormal | 0: Normal 1: Fault
3 | Group 1 Reserved | 0: Normal 1: Fault |  | 3 | Group 4 Reserved | 0: Normal 1: Fault
4 | Group 1 Voltage Sampling Circuit Disconnected | 0: Normal 1: Fault |  | 4 | Group 4 Voltage Sampling Circuit Disconnected | 0: Normal 1: Fault
5 | Group 1 Temperature Sampling Circuit Disconnected | 0: Normal 1: Fault |  | 5 | Group 4 Temperature Sampling Circuit Disconnected | 0: Normal 1: Fault
6 | Group 1 Main-sub & Interior CAN Disconnected | 0: Normal 1: Fault |  | 6 | Group 4 Main-sub Interior CAN Disconnected | 0: Normal 1: Fault
7 | Group 1 Reserved | 0: Normal 1: Fault |  | 7 | Group 4 Reserved | 0: Normal 1: Fault
8 | Group 1 Reserved | 0: Normal 1: Fault |  | 8 | Group 4 Reserved | 0: Normal 1: Fault
9 | Group 1 Current Sampling Circuit Failure | 0: Normal 1: Fault |  | 9 | Group 4 Current Sampling Circuit Failure | 0: Normal 1: Fault
10 | Group 1 Battery Cell Failure | 0: Normal 1: Fault |  | 10 | Group 4 Battery Cell Failure | 0: Normal 1: Fault
11 | Group 1 Main Contactor Abnormal | 0: Normal 1: Fault |  | 11 | Group 4 main contactor abnormal | 0: Normal 1: Fault
12 | Group 1 Pre-charging Contactor Abnormal | 0: Normal 1: Fault |  | 12 | Group 4 Pre-charging contactor abnormal | 0: Normal 1: Fault
13 | Group 1 Reserved | 0: Normal 1: Fault |  | 13 | Group 4 Reserved | 0: Normal 1: Fault
14 | Group 1 BMU Power Contactor Abnormal | 0: Normal 1: Fault |  | 14 | Group 4 BMU Power contactor abnormal | 0: Normal 1: Fault
15 | Group 1 Reserved | 0: Normal 1: Fault |  | 15 | Group 4 Reserved | 0: Normal 1: Fault
Group 1 Fault Information 1 |  |  |  | Group 4 Fault Information 1
No. | Definition | Value/Status |  | No. | Definition | Value/Status
0 | Group 1 Reserved | 0: Normal 1: Fault |  | 0 | Group 4 Reserved | 0: Normal 1: Fault
1 | Group 1 Reserved | 0: Normal 1: Fault |  | 1 | Group 4 Reserved | 0: Normal 1: Fault
2 | Group 1 Serious High-temperature Failure | 0: Normal 1: Fault |  | 2 | Group 4 Serious High-temperature Failure | 0: Normal 1: Fault
3 | Group 1 Reserved | 0: Normal 1: Fault |  | 3 | Group 4 Reserved | 0: Normal 1: Fault
4 | Group 1 Reserved | 0: Normal 1: Fault |  | 4 | Group 4 Reserved | 0: Normal 1: Fault
5 | Group 1 Reserved | 0: Normal 1: Fault |  | 5 | Group 4 Reserved | 0: Normal 1: Fault
6 | Group 1 Reserved | 0: Normal 1: Fault |  | 6 | Group 4 Reserved | 0: Normal 1: Fault
7 | Group 1 Reserved | 0: Normal 1: Fault |  | 7 | Group 4 Reserved | 0: Normal 1: Fault
8 | Group 1 Fuse Protector Failure | 0: Normal 1: Fault |  | 8 | Group 4 Fuse Protector Failure | 0: Normal 1: Fault
9 | Group 1 Reserved | 0: Normal 1: Fault |  | 9 | Group 4 Reserved | 0: Normal 1: Fault
10 | Group 1 Reserved | 0: Normal 1: Fault |  | 10 | Group 4 Reserved | 0: Normal 1: Fault
11 | Group 1 Reserved | 0: Normal 1: Fault |  | 11 | Group 4 Reserved | 0: Normal 1: Fault
12 | Grouo 1 Disconnected with Stack Communication CAN | 0: Normal 1: Fault |  | 12 | Group 4 Disconnected with Stack Communication CAN | 0: Normal 1: Fault
13 | Group 1 Reserved | 0: Normal 1: Fault |  | 13 | Group 4 Reserved | 0: Normal 1: Fault
14 | Group 1 BMU Power Contactor Disconnected | 0: Normal 1: Fault |  | 14 | Group 4 BMU Power Contactor Disconnected | 0: Normal 1: Fault
15 | Group 1 Reserved | 0: Normal 1: Fault |  | 15 | Group 4 Reserved | 0: Normal 1: Fault

## Warning List
Stack Warning Information 0
No. | Definition | Value/Status |  | Inverter Warning Inforamtion 1
0 | Stack Charging Common Over-current Warning | 0: Normal 1:Warning | new BitItemOnOff(0, "Stack Charging Common Over-current Warning"), | No. | Definition | Value/Status
1 | Stack Disharging Common Over-current Warning | 0: Normal 1:Warning | new BitItemOnOff(1, "Stack Disharging Common Over-current Warning"), | 0 | Grid Under-Voltage | 0: Normal 1:Warning | new BitItemOnOff(0, "Grid Under-Voltage"),
2 | Stack Charging Current Limited Warning | 0: Normal 1:Warning | new BitItemOnOff(2, "Stack Charging Current Limited Warning"), | 1 | Grid Over-Voltage | 0: Normal 1:Warning | new BitItemOnOff(1, "Grid Over-Voltage"),
3 | Stack Discharging Current Limited Warning | 0: Normal 1:Warning | new BitItemOnOff(3, "Stack Discharging Current Limited Warning"), | 2 | Grid under-Frequency | 0: Normal 1:Warning | new BitItemOnOff(2, "Grid under-Frequency"),
4 | Stack Common High-voltage Warning | 0: Normal 1:Warning | new BitItemOnOff(4, "Stack Common High-voltage Warning"), | 3 | Grid Over-Frequency | 0: Normal 1:Warning | new BitItemOnOff(3, "Grid Over-Frequency"),
5 | Stack Common Low-voltage Warning | 0: Normal 1:Warning | new BitItemOnOff(5, "Stack Common Low-voltage Warning"), | 4 | Grid flicker | 0: Normal 1:Warning | new BitItemOnOff(4, "Grid flicker"),
6 | Stack Voltage Change Abnormal Warning | 0: Normal 1:Warning | new BitItemOnOff(6, "Stack Voltage Change Abnormal Warning"), | 5 | Grid Abnormal | 0: Normal 1:Warning | new BitItemOnOff(5, "Grid Abnormal"),
7 | Stack Common High-temperature Warning | 0: Normal 1:Warning | new BitItemOnOff(7, "Stack Common High-temperature Warning"), | 6 | DC Under-Voltage | 0: Normal 1:Warning | new BitItemOnOff(6, "DC Under-Voltage"),
8 | Stack Common Low-temperature Warning | 0: Normal 1:Warning | new BitItemOnOff(8, "Stack Common Low-temperature Warning"), | 7 | Input Over-resistance | 0: Normal 1:Warning | new BitItemOnOff(7, "Input Over-resistance"),
9 | Stack Temperature Change Abnormal Warning | 0: Normal 1:Warning | new BitItemOnOff(9, "Stack Temperature Change Abnormal Warning"), | 8 | Combine Jumper Settings Wrong | 0: Normal 1:Warning | new BitItemOnOff(8, "Combine Jumper Settings Wrong"),
10 | Stack Serious High-voltage Warning | 0: Normal 1:Warning | new BitItemOnOff(10, "Stack Serious High-voltage Warning"), | 9 | Communication with Inverter failure | 0: Normal 1:Warning | new BitItemOnOff(9, "Communication with Inverter failure"),
11 | Stack Serious Low-voltage Warning | 0: Normal 1:Warning | new BitItemOnOff(11, "Stack Serious Low-voltage Warning"), | 10 | System Time Failure | 0: Normal 1:Warning | new BitItemOnOff(10, "System Time Failure"),
12 | Stack Serious Low-tempature Warning | 0: Normal 1:Warning | new BitItemOnOff(12, "Stack Serious Low-tempature Warning"), | 11 | Reserved | 0: Normal 1:Warning | new BitItemOnOff(11, "Reserved"),
13 | Stack Charging Serious Over-current Warning | 0: Normal 1:Warning | new BitItemOnOff(13, "Stack Charging Serious Over-current Warning"), | 12 | Reserved | 0: Normal 1:Warning | new BitItemOnOff(12, "Reserved"),
14 | Stack Discharging Serious Over-current Warning | 0: Normal 1:Warning | new BitItemOnOff(14, "Stack Discharging Serious Over-current Warning"), | 13 | Reserved | 0: Normal 1:Warning | new BitItemOnOff(13, "Reserved"),
15 | Stack Battery Capacity Abnormal Warning | 0: Normal 1:Warning | new BitItemOnOff(15, "Stack Battery Capacity Abnormal Warning"), | 14 | Reserved | 0: Normal 1:Warning | new BitItemOnOff(14, "Reserved"),
Stack Warning Information 1 |  |  |  | 15 | Reserved | 0: Normal 1:Warning | new BitItemOnOff(15, "Reserved"),
No. | Definition | Value/Status |  | Inverter Warning Inforamtion 2
0 | Stack EEPROM Parameter Failure | 0: Normal 1:Warning | new BitItemOnOff(0, "Stack EEPROM Parameter Failure"), | No. | Definition | Value/Status
1 | Combiner Cabinet Isolation Swtich Disconnected | 0: Normal 1:Warning | new BitItemOnOff(1, "Combiner Cabinet Isolation Swtich Disconnected"), | 0 | Reserved | 0: Normal 1:Warning | new BitItemOnOff(0, "Reserved"),
2 | Communication Disconnected between Stack and Temperature Collector | 0: Normal 1:Warning | new BitItemOnOff(2, "Communication Disconnected between Stack and Temperature Collector"), | 1 | Reserved | 0: Normal 1:Warning | new BitItemOnOff(1, "Reserved"),
3 | Tempature Collector Failure | 0: Normal 1:Warning | new BitItemOnOff(3, "Tempature Collector Failure"), | 2 | Reserved | 0: Normal 1:Warning | new BitItemOnOff(2, "Reserved"),
4 | Hall Inaccurate | 0: Normal 1:Warning | new BitItemOnOff(4, "Hall Inaccurate"), | 3 | Reserved | 0: Normal 1:Warning | new BitItemOnOff(3, "Reserved"),
5 | PCS Communication Failure | 0: Normal 1:Warning | new BitItemOnOff(5, "PCS Communication Failure"), | 4 | Reserved | 0: Normal 1:Warning | new BitItemOnOff(4, "Reserved"),
6 | Pre-charging or Main Contactor Abnormal Engaged | 0: Normal 1:Warning | new BitItemOnOff(6, "Pre-charging or Main Contactor Abnormal Engaged"), | 5 | Reserved | 0: Normal 1:Warning | new BitItemOnOff(5, "Reserved"),
7 | Voltage Sampling Abnormal | 0: Normal 1:Warning | new BitItemOnOff(7, "Voltage Sampling Abnormal"), | 6 | Reserved | 0: Normal 1:Warning | new BitItemOnOff(6, "Reserved"),
8 | Pre-charging Contactor Abnormal or PCS485 Channel Abnormal | 0: Normal 1:Warning | new BitItemOnOff(8, "Pre-charging Contactor Abnormal or PCS485 Channel Abnormal"), | 7 | Reserved | 0: Normal 1:Warning | new BitItemOnOff(7, "Reserved"),
9 | Main Contactor Abnormal | 0: Normal 1:Warning | new BitItemOnOff(9, "Main Contactor Abnormal"), | 8 | Reserved | 0: Normal 1:Warning | new BitItemOnOff(8, "Reserved"),
10 | Reserved | 0: Normal 1:Warning | new BitItemOnOff(10, "Reserved"), | 9 | Reserved | 0: Normal 1:Warning | new BitItemOnOff(9, "Reserved"),
11 | Reserved | 0: Normal 1:Warning | new BitItemOnOff(11, "Reserved"), | 10 | Reserved | 0: Normal 1:Warning | new BitItemOnOff(10, "Reserved"),
12 | Reserved | 0: Normal 1:Warning | new BitItemOnOff(12, "Reserved"), | 11 | Reserved | 0: Normal 1:Warning | new BitItemOnOff(11, "Reserved"),
13 | Reserved | 0: Normal 1:Warning | new BitItemOnOff(13, "Reserved"), | 12 | Reserved | 0: Normal 1:Warning | new BitItemOnOff(12, "Reserved"),
14 | Reserved | 0: Normal 1:Warning | new BitItemOnOff(14, "Reserved"), | 13 | Reserved | 0: Normal 1:Warning | new BitItemOnOff(13, "Reserved"),
15 | Reserved | 0: Normal 1:Warning | new BitItemOnOff(15, "Reserved"), | 14 | Reserved | 0: Normal 1:Warning | new BitItemOnOff(14, "Reserved"),
|  |  |  | 15 | Reserved | 0: Normal 1:Warning | new BitItemOnOff(15, "Reserved"),
Group 0 Warning Information 0
No. | Definition | Value/Status |  | Charger Warning Inforamtion
0 | Group 0 Charging Common Over-current Warning | 0: Normal 1:Warning |  | No. | Definition | Value/Status
1 | Group 0 Discharging Common Over-current Warning | 0: Normal 1:Warning |  | 0 | Input Over-Voltage | 0: Normal 1:Warning | new BitItemOnOff(0, "Input Over-Voltage"),
2 | Group 0 Charging Current Limited Warning | 0: Normal 1:Warning |  | 1 | Input Under-Voltage | 0: Normal 1:Warning | new BitItemOnOff(1, "Input Under-Voltage"),
3 | Group 0 Discharging Current Limited Warning | 0: Normal 1:Warning |  | 2 | PV Under-Voltage | 0: Normal 1:Warning | new BitItemOnOff(2, "PV Under-Voltage"),
4 | Group 0 Common High-voltage Warning | 0: Normal 1:Warning |  | 3 | Fan Failure | 0: Normal 1:Warning | new BitItemOnOff(3, "Fan Failure"),
5 | Group 0 Common Low-voltage Warning | 0: Normal 1:Warning |  | 4 |  | 0: Normal 1:Warning | new BitItemOnOff(4, ""),
6 | Group 0 Voltage Change Abnormal Warning | 0: Normal 1:Warning |  | 5 | Commnication Failure | 0: Normal 1:Warning | new BitItemOnOff(5, "Commnication Failure"),
7 | Group 0 Common High-temperature Warning | 0: Normal 1:Warning |  | 6 | Reserved | 0: Normal 1:Warning | new BitItemOnOff(6, "Reserved"),
8 | Group 0 Common Low-temperature Warning | 0: Normal 1:Warning |  | 7 | Reserved | 0: Normal 1:Warning | new BitItemOnOff(7, "Reserved"),
9 | Group 0 Temperature Change Abnormal Warning | 0: Normal 1:Warning |  | 8 | Reserved | 0: Normal 1:Warning | new BitItemOnOff(8, "Reserved"),
10 | Group 0 Serious High-voltage Warning | 0: Normal 1:Warning |  | 9 | Reserved | 0: Normal 1:Warning | new BitItemOnOff(9, "Reserved"),
11 | Group 0 Serious Low-voltage Warning | 0: Normal 1:Warning |  | 10 | Reserved | 0: Normal 1:Warning | new BitItemOnOff(10, "Reserved"),
12 | Group 0 Serious Low-tempature Warning | 0: Normal 1:Warning |  | 11 | Reserved | 0: Normal 1:Warning | new BitItemOnOff(11, "Reserved"),
13 | Group 0 Charging Serious Over-current Warning | 0: Normal 1:Warning |  | 12 | Reserved | 0: Normal 1:Warning | new BitItemOnOff(12, "Reserved"),
14 | Group 0 Discharging Serious Over-current Warning | 0: Normal 1:Warning |  | 13 | Reserved | 0: Normal 1:Warning | new BitItemOnOff(13, "Reserved"),
15 | Group 0 Battery Capacity Abnormal Warning | 0: Normal 1:Warning |  | 14 | Reserved | 0: Normal 1:Warning | new BitItemOnOff(14, "Reserved"),
Group 0 Warning Information 1 |  |  |  | 15 | Reserved | 0: Normal 1:Warning | new BitItemOnOff(15, "Reserved"),
No. | Definition | Value/Status
0 | Equilibrium Sampling Abnormal Warning | 0: Normal 1:Warning |  | Group 3 Warning Information 0
1 | Equilibrium Control Abnormal Warning | 0: Normal 1:Warning |  | No. | Definition | Value/Status
2 | Hall Inaccurate | 0: Normal 1:Warning |  | 0 | Group 3 Charging Common Over-current Warning | 0: Normal 1:Warning
3 | Reserved | 0: Normal 1:Warning |  | 1 | Group 3 Discharging Common Over-current Warning | 0: Normal 1:Warning
4 | Reserved | 0: Normal 1:Warning |  | 2 | Group 3 Charging Current Limited Warning | 0: Normal 1:Warning
5 | Reserved | 0: Normal 1:Warning |  | 3 | Group 3 Discharging Current Limited Warning | 0: Normal 1:Warning
6 | Reserved | 0: Normal 1:Warning |  | 4 | Group 3 Common High-voltage Warning | 0: Normal 1:Warning
7 | Reserved | 0: Normal 1:Warning |  | 5 | Group 3 Common Low-voltage Warning | 0: Normal 1:Warning
8 | Reserved | 0: Normal 1:Warning |  | 6 | Group 3 Voltage Change Abnormal Warning | 0: Normal 1:Warning
9 | Reserved | 0: Normal 1:Warning |  | 7 | Group 3 Common High-temperature Warning | 0: Normal 1:Warning
10 | Reserved | 0: Normal 1:Warning |  | 8 | Group 3 Common Low-temperature Warning | 0: Normal 1:Warning
11 | Reserved | 0: Normal 1:Warning |  | 9 | Group 3 Temperature Change Abnormal Warning | 0: Normal 1:Warning
12 | Reserved | 0: Normal 1:Warning |  | 10 | Group 3 Serious High-voltage Warning | 0: Normal 1:Warning
13 | High-voltage Offset | 0: Normal 1:Warning |  | 11 | Group 3 Serious Low-voltage Warning | 0: Normal 1:Warning
14 | Low-voltage Offset | 0: Normal 1:Warning |  | 12 | Group 3 Serious Low-tempature Warning | 0: Normal 1:Warning
15 | High-temperature Offset | 0: Normal 1:Warning |  | 13 | Group 3 Charging Serious Over-current Warning | 0: Normal 1:Warning
|  |  |  | 14 | Group 3 Discharging Serious Over-current Warning | 0: Normal 1:Warning
Group 1 Warning Information 0 |  |  |  | 15 | Group 3 Battery Capacity Abnormal Warning | 0: Normal 1:Warning
No. | Definition | Value/Status |  | Group 3 Warning Information 1
0 | Group 1 Charging Common Over-current Warning | 0: Normal 1:Warning |  | No. | Definition | Value/Status
1 | Group 1 Discharging Common Over-current Warning | 0: Normal 1:Warning |  | 0 | Equilibrium Sampling Abnormal Warning | 0: Normal 1:Warning
2 | Group 1 Charging Current Limited Warning | 0: Normal 1:Warning |  | 1 | Equilibrium Control Abnormal Warning | 0: Normal 1:Warning
3 | Group 1 Discharging Current Limited Warning | 0: Normal 1:Warning |  | 2 | Hall Inaccurate | 0: Normal 1:Warning
4 | Group 1 Common High-voltage Warning | 0: Normal 1:Warning |  | 3 | Reserved | 0: Normal 1:Warning
5 | Group 1 Common Low-voltage Warning | 0: Normal 1:Warning |  | 4 | Reserved | 0: Normal 1:Warning
6 | Group 1 Voltage Change Abnormal Warning | 0: Normal 1:Warning |  | 5 | Reserved | 0: Normal 1:Warning
7 | Group 1 Common High-temperature Warning | 0: Normal 1:Warning |  | 6 | Reserved | 0: Normal 1:Warning
8 | Group 1 Common Low-temperature Warning | 0: Normal 1:Warning |  | 7 | Reserved | 0: Normal 1:Warning
9 | Group 1 Temperature Change Abnormal Warning | 0: Normal 1:Warning |  | 8 | Reserved | 0: Normal 1:Warning
10 | Group 1 Serious High-voltage Warning | 0: Normal 1:Warning |  | 9 | Reserved | 0: Normal 1:Warning
11 | Group 1 Serious Low-voltage Warning | 0: Normal 1:Warning |  | 10 | Reserved | 0: Normal 1:Warning
12 | Group 1 Serious Low-tempature Warning | 0: Normal 1:Warning |  | 11 | Reserved | 0: Normal 1:Warning
13 | Group 1 Charging Serious Over-current Warning | 0: Normal 1:Warning |  | 12 | Reserved | 0: Normal 1:Warning
14 | Group 1 Discharging Serious Over-current Warning | 0: Normal 1:Warning |  | 13 | High-voltage Approach warning | 0: Normal 1:Warning
15 | Group 1 Battery Capacity Abnormal Warning | 0: Normal 1:Warning |  | 14 | Low-voltage Approach warning | 0: Normal 1:Warning
Group 1 Warning Information 1 |  | 0: Normal 1:Warning |  | 15 | High-temperature Approach warning | 0: Normal 1:Warning
No. | Definition | Value/Status
0 | Equilibrium Sampling Abnormal Warning | 0: Normal 1:Warning |  | Stack Warning Information 2
1 | Equilibrium Control Abnormal Warning | 0: Normal 1:Warning |  | No. | Definition | Value/Status
2 | Hall Inaccurate | 0: Normal 1:Warning |  | 0 | Group 0 Enabling Unable to Be On-grid | 0: Normal 1:Warning | new BitItemOnOff(0, "Group 0 Enabling Unable to Be On-grid"),
3 | Reserved | 0: Normal 1:Warning |  | 1 | Group 1 Enabling Unable to Be On-grid | 0: Normal 1:Warning | new BitItemOnOff(1, "Group 1 Enabling Unable to Be On-grid"),
4 | Reserved | 0: Normal 1:Warning |  | 2 | Group 2 Enabling Unable to Be On-grid | 0: Normal 1:Warning | new BitItemOnOff(2, "Group 2 Enabling Unable to Be On-grid"),
5 | Reserved | 0: Normal 1:Warning |  | 3 | Group 3 Enabling Unable to Be On-grid | 0: Normal 1:Warning | new BitItemOnOff(3, "Group 3 Enabling Unable to Be On-grid"),
6 | Reserved | 0: Normal 1:Warning |  | 4 | Group 4 Enabling Unable to Be On-grid | 0: Normal 1:Warning | new BitItemOnOff(4, "Group 4 Enabling Unable to Be On-grid"),
7 | Reserved | 0: Normal 1:Warning |  | 5 | Group 5 Enabling Unable to Be On-grid | 0: Normal 1:Warning | new BitItemOnOff(5, "Group 5 Enabling Unable to Be On-grid"),
8 | Reserved | 0: Normal 1:Warning |  | 6 | Group 6 Enabling Unable to Be On-grid | 0: Normal 1:Warning | new BitItemOnOff(6, "Group 6 Enabling Unable to Be On-grid"),
9 | Reserved | 0: Normal 1:Warning |  | 7 | Group 7 Enabling Unable to Be On-grid | 0: Normal 1:Warning | new BitItemOnOff(7, "Group 7 Enabling Unable to Be On-grid"),
10 | Reserved | 0: Normal 1:Warning |  | 8 | Group 8 Enabling Unable to Be On-grid | 0: Normal 1:Warning | new BitItemOnOff(8, "Group 8 Enabling Unable to Be On-grid"),
11 | Reserved | 0: Normal 1:Warning |  | 9 | Group 9 Enabling Unable to Be On-grid | 0: Normal 1:Warning | new BitItemOnOff(9, "Group 9 Enabling Unable to Be On-grid"),
12 | Reserved | 0: Normal 1:Warning |  | 10 | Group 10 Enabling Unable to Be On-grid | 0: Normal 1:Warning | new BitItemOnOff(10, "Group 10 Enabling Unable to Be On-grid"),
13 | High-voltage Offset | 0: Normal 1:Warning |  | 11 | Group 11 Enabling Unable to Be On-grid | 0: Normal 1:Warning | new BitItemOnOff(11, "Group 11 Enabling Unable to Be On-grid"),
14 | Low-voltage Offset | 0: Normal 1:Warning |  | 12 | Group 12 Enabling Unable to Be On-grid | 0: Normal 1:Warning | new BitItemOnOff(12, "Group 12 Enabling Unable to Be On-grid"),
15 | High-temperature Offset | 0: Normal 1:Warning |  | 13 | Group 13 Enabling Unable to Be On-grid | 0: Normal 1:Warning | new BitItemOnOff(13, "Group 13 Enabling Unable to Be On-grid"),
Group 1 Warning Information 0 |  |  |  | 14 | Group 14 Enabling Unable to Be On-grid | 0: Normal 1:Warning | new BitItemOnOff(14, "Group 14 Enabling Unable to Be On-grid"),
No. | Definition | Value/Status |  | 15 | Group 15 Enabling Unable to Be On-grid | 0: Normal 1:Warning | new BitItemOnOff(15, "Group 15 Enabling Unable to Be On-grid"),
0 | Group 2 Charging Common Over-current Warning | 0: Normal 1:Warning |  | Stack Warning Information 3
1 | Group 2 Discharging Common Over-current Warning | 0: Normal 1:Warning |  | No. | Definition | Value/Status
2 | Group 2 Charging Current Limited Warning | 0: Normal 1:Warning |  | 0 | Group 0 Isolation Switch Open | 0: Normal 1:Warning | new BitItemOnOff(0, "Group 0 Isolation Switch Open"),
3 | Group 2 Discharging Current Limited Warning | 0: Normal 1:Warning |  | 1 | Group 1 Isolation Switch Open | 0: Normal 1:Warning | new BitItemOnOff(1, "Group 1 Isolation Switch Open"),
4 | Group 2 Common High-voltage Warning | 0: Normal 1:Warning |  | 2 | Group 2 Isolation Switch Open | 0: Normal 1:Warning | new BitItemOnOff(2, "Group 2 Isolation Switch Open"),
5 | Group 2 Common Low-voltage Warning | 0: Normal 1:Warning |  | 3 | Group 3 Isolation Switch Open | 0: Normal 1:Warning | new BitItemOnOff(3, "Group 3 Isolation Switch Open"),
6 | Group 2 Voltage Change Abnormal Warning | 0: Normal 1:Warning |  | 4 | Group 4 Isolation Switch Open | 0: Normal 1:Warning | new BitItemOnOff(4, "Group 4 Isolation Switch Open"),
7 | Group 2 Common High-temperature Warning | 0: Normal 1:Warning |  | 5 | Group 5 Isolation Switch Open | 0: Normal 1:Warning | new BitItemOnOff(5, "Group 5 Isolation Switch Open"),
8 | Group 2 Common Low-temperature Warning | 0: Normal 1:Warning |  | 6 | Group 6 Isolation Switch Open | 0: Normal 1:Warning | new BitItemOnOff(6, "Group 6 Isolation Switch Open"),
9 | Group 2 Temperature Change Abnormal Warning | 0: Normal 1:Warning |  | 7 | Group 7 Isolation Switch Open | 0: Normal 1:Warning | new BitItemOnOff(7, "Group 7 Isolation Switch Open"),
10 | Group 2 Serious High-voltage Warning | 0: Normal 1:Warning |  | 8 | Group 8 Isolation Switch Open | 0: Normal 1:Warning | new BitItemOnOff(8, "Group 8 Isolation Switch Open"),
11 | Group 2 Serious Low-voltage Warning | 0: Normal 1:Warning |  | 9 | Group 9 Isolation Switch Open | 0: Normal 1:Warning | new BitItemOnOff(9, "Group 9 Isolation Switch Open"),
12 | Group 2 Serious Low-tempature Warning | 0: Normal 1:Warning |  | 10 | Group 10 Isolation Switch Open | 0: Normal 1:Warning | new BitItemOnOff(10, "Group 10 Isolation Switch Open"),
13 | Group 2 Charging Serious Over-current Warning | 0: Normal 1:Warning |  | 11 | Group 11 Isolation Switch Open | 0: Normal 1:Warning | new BitItemOnOff(11, "Group 11 Isolation Switch Open"),
14 | Group 2 Discharging Serious Over-current Warning | 0: Normal 1:Warning |  | 12 | Group 12 Isolation Switch Open | 0: Normal 1:Warning | new BitItemOnOff(12, "Group 12 Isolation Switch Open"),
15 | Group 2 Battery Capacity Abnormal Warning | 0: Normal 1:Warning |  | 13 | Group 13 Isolation Switch Open | 0: Normal 1:Warning | new BitItemOnOff(13, "Group 13 Isolation Switch Open"),
Group 2 Warning Information 1 |  |  |  | 14 | Group 14 Isolation Switch Open | 0: Normal 1:Warning | new BitItemOnOff(14, "Group 14 Isolation Switch Open"),
No. | Definition | Value/Status |  | 15 | Group 15 Isolation Switch Open | 0: Normal 1:Warning | new BitItemOnOff(15, "Group 15 Isolation Switch Open"),
0 | Equilibrium Sampling Abnormal Warning | 0: Normal 1:Warning |  | Stack Warning Information 4
1 | Equilibrium Control Abnormal Warning | 0: Normal 1:Warning |  | No. | Definition | Value/Status
2 | Hall Inaccurate | 0: Normal 1:Warning |  | 0 | Reserved | 0: Normal 1:Warning | new BitItemOnOff(0, "Reserved"),
3 | Reserved | 0: Normal 1:Warning |  | 1 | Reserved | 0: Normal 1:Warning | new BitItemOnOff(1, "Reserved"),
4 | Reserved | 0: Normal 1:Warning |  | 2 | Reserved | 0: Normal 1:Warning | new BitItemOnOff(2, "Reserved"),
5 | Reserved | 0: Normal 1:Warning |  | 3 | Reserved | 0: Normal 1:Warning | new BitItemOnOff(3, "Reserved"),
6 | Reserved | 0: Normal 1:Warning |  | 4 | Reserved | 0: Normal 1:Warning | new BitItemOnOff(4, "Reserved"),
7 | Reserved | 0: Normal 1:Warning |  | 5 | Reserved | 0: Normal 1:Warning | new BitItemOnOff(5, "Reserved"),
8 | Reserved | 0: Normal 1:Warning |  | 6 | Reserved | 0: Normal 1:Warning | new BitItemOnOff(6, "Reserved"),
9 | Reserved | 0: Normal 1:Warning |  | 7 | Reserved | 0: Normal 1:Warning | new BitItemOnOff(7, "Reserved"),
10 | Reserved | 0: Normal 1:Warning |  | 8 | Reserved | 0: Normal 1:Warning | new BitItemOnOff(8, "Reserved"),
11 | Reserved | 0: Normal 1:Warning |  | 9 | Reserved | 0: Normal 1:Warning | new BitItemOnOff(9, "Reserved"),
12 | Reserved | 0: Normal 1:Warning |  | 10 | Reserved | 0: Normal 1:Warning | new BitItemOnOff(10, "Reserved"),
13 | High-voltage Offset | 0: Normal 1:Warning |  | 11 | Reserved | 0: Normal 1:Warning | new BitItemOnOff(11, "Reserved"),
14 | Low-voltage Offset | 0: Normal 1:Warning |  | 12 | Reserved | 0: Normal 1:Warning | new BitItemOnOff(12, "Reserved"),
15 | High-temperature Offset | 0: Normal 1:Warning |  | 13 | Reserved | 0: Normal 1:Warning | new BitItemOnOff(13, "Reserved"),
|  |  |  | 14 | Reserved | 0: Normal 1:Warning | new BitItemOnOff(14, "Reserved"),
|  |  |  | 15 | Reserved | 0: Normal 1:Warning | new BitItemOnOff(15, "Reserved"),