## Slide 1: On the Importance of the Azimuth Offset for 2P Individual Pitch Control
WESC 2019, Cork, Ireland. June 19, 2019.
Sebastiaan Mulders and Jan-Willem van Wingerden
Notes: Good afternoon everyone, I am Sebastiaan Mulders, a PhD candidate at the Delft University of Technology, and today I will be presenting a quite in depth topic on Individual Pitch Control for wind turbines, called the azimuth offset.

## Slide 2: Why Individual Pitch Control (IPC)?
Source: Rishabh Dev Sharma
Introduction Recap MBC Decoupling analysis High-fidelity results
Notes: But first, what is individual pitch control, in short IPC, and why would we need it? As you can see in this video, a camera is mounted at the blade root. What you immidiately see is that the blade has an out-of-plane flapping motion. While this motion seems not that severe, imagine that a wind turbine has to endure this for its total 20 year life span. This load will inevitably lead to material fatigue, and this is the reason thaat we use individual pitch control, to reduce these oscillations by individually pitching the blades.

## Slide 3: Where do these oscillations come from?
Wind shear
Tower shadow
Introduction Recap MBC Decoupling analysis High-fidelity results
Notes: But where do these oscillations come from? What you see here is a nice wind turbine, and a wind field hitting the wind turbine. What is immediately apparent is that the wind speed is lower at ground level, and stronger at higher levels. Also, each blade passes the tower once in every revolution, which causes the blade to experience a wind speed speed deficit. These two effects are the main contributions for the 1P and the nP harmonics that are present when you would inspect the blade root moment power spectrum.

## Slide 4: The general implementation of IPC
Introduction Recap MBC Decoupling analysis High-fidelity results
θ2
θ3
My,2
My,1
My,3
θ1
Wind turbine
MBC-1 ()
(1P)
MBC()
(1P)
MBC-1 ()
(2P)
MBC()
(2P)
Notes: So now let’s look how individual pitch control is generally implemented in a simplified control block scheme. First I define the in- and outputs. The outputs are indicated in red, and are the blade root out of plane moments, so moving in and out of the screen as indicated by these dart symbols. These moments need to be reduced by pitching the blades individually by THETA, and are indicated by the green arrows.
Now we build up out control scheme. So wind turbine with pitch inputs and blade moments outputs. The outputs are fed to the forward azimuth dependent transformation. Why this is done will be explained shortly, but just believe me for a second. Then there come out two signals from the transformation, to which we apply integral control. Then, we do the exact same, but inverse transformation, and we obtain our individual pitch contributions.
I want to stress again that these apparently needed transformations are a function of the current azimuth position. However, some publications propose to include an offset to this azimuth position in the reverse transformation. However, until recently it was ambigious why this offset was needed, and what it actually does.

## Slide 5: The azimuth offset: what do scientists say?
“A constant offset can account for the remaining interaction between the two transformed axes” [1]
“The offset is used to account for the phase lag between the controller and pitch actuator” [2]
“The azimuth offset changes the IPC dynamics, and an optimum is present in terms of DEL” [3]
“The azimuth offset is needed for successful attenuation of the 1P and 2P harmonics” [4]
CONFUSION
Introduction Recap MBC Decoupling analysis High-fidelity results
Notes: So let’s have a look what the scientists say, references will be given in the last slide.
One scientist says that that a CONSTANT OFFSET needs to be incorporated to account for the remaining interactions between the transformed axes
Then, another scientist says that the offset is used to account for the phase lag between the controller an the actuator.
Yet another scientist says that it can be concluded that in terms of fatigue loads, an optimal value of azimuth offset is present,
Then, the last scientist says that for succesfull attenuation of 1P and 2P harmonics, you need different offsets for both control loops.
So , as you all can see, the scientists, do not agree, and there is a lot of confusion going on here in this situation.

## Slide 6: Further analysis on the azimuth offset
Published in Wind Energy
Focus on analysis and 1P
Accepted for ACC2019
Focus on performance at 2P
Introduction Recap MBC Decoupling analysis High-fidelity results
Notes: To stop the confusion, I worked on a couple of publications. So first we published a journal article in Wind Energy, where we do a frequency-domain analysis on the offset, we focus on 1P, but we do not yet show an in-depth analysis of the load reduction benefits. A more practical paper is submitted and will be presented at the American Control Conference next monts, where we show that the azimuth offset is really needed for succelfull attenuation of the 1P+2P loading on your blades.

## Slide 7: Focus of this presentation on 2P
Wind turbine
MBC-1 ()
(1P)
MBC ()
(1P)
MBC-1 ()
(2P)
MBC()
(2P)
Quick recap of the Multi-Blade Coordinate MBC transformation
Control decoupling and sensitivity analysis on the 2P load
High-fidelity results on the NREL 5-MW turbine for 1P+2P loads
Introduction Recap MBC Decoupling analysis High-fidelity results
Notes: So now the focus of this presentation. As I already said, we published a paper on the analysis of the 1P azimuth offset, but in this presentation we will add a 2P load reduction feedback loop, and also see what the benefit is by including the azimuth offset.
The remainder of this presentation is structured as follows.
First I will give a quick recap on how the Multi-Blade Coordinate transformation works.
Then I will do a control sensitivity analysis on incorporating this azimuth offset for 2P
And finally I will perform some high fidelity simulations, using the NREL 5-MW wind turbine for reduction of a combined 1P + 2P implementation

## Slide 8: The Multi-Blade Coordinate transformation
The rotating coordinate system
θ2
θ1
θ3
My,2
My,1
My,3
Wind turbine
Introduction Recap MBC Decoupling analysis High-fidelity results
Notes: So again, we have our wind turbine with the blade moment outputs and the pitch inputs. We make a block scheme of our wind turbine, and move the in- and outputs. Then, what we do is that we look at frequency magnitude response at different azimuth angles. What we now see happening is that the dynamics change with the azimuth position. From a control perspective this is bad, because this means that we would require a more complex controller that also varies with the azimuth position of the turbine.

## Slide 9: The Multi-Blade Coordinate transformation
The non-rotating coordinate system
θtilt
θyaw
Mtilt
Myaw
Wind turbine
MBC()
MBC-1 ()
Introduction Recap MBC Decoupling analysis High-fidelity results
Notes: So to solve this problem, we introduce the MBC transformation. So we put on the forward transformation, and the reverse transformation around our wind turbine: and we are left with two in and output signals instead of 3. And what the nice thing is on this transformation is that we have a non-rotating framework, so we have a virtual tilt and yaw, moment and pitch signal. The good thing is is that when we look at the frequency magnitude response, that especially in the low-frequency region, the trajectory stays the same, which is beneficial for more convenient control deisgn.

## Slide 10: Reduction of coupling
Wind turbine
MBC()
MBC-1 ()
θtilt
θyaw
Mtilt
Myaw
Introduction Recap MBC Decoupling analysis High-fidelity results
Notes: But there is a catch, when we do this transformation, but not include the azimuth offset.
So we first consider this whole open-loop system as as single block. What we ideally want to achieve is that everything that we do with the virtual tilt pitch angle only affects the tilt moment. Likewise with the yaw pitch and moment.
But in reality, we will see that there is coupling present between the two axes. So if you do something with the tilt pitch angle, this affects the yaw moment. And we don’t want this. These plots show the amount of diagonal contribution, and the amount of off-diagonal interactions, and you see that for the 2P implementation, you have more interaction, than cirect contribution.
The nice thing is now, that when we use the azimuth offset and set it to the optimal value, we can basically minimize the interactions, which is a thing we want. At the same time, the direct path remains largely unaffected.

## Slide 11: Control sensitivity analysis
The azimuth offset as a tuning knob
AZIMUTH OFFSET
Off
Opt
Introduction Recap MBC Decoupling analysis High-fidelity results
Notes: So let’s do the same trick for the sensitivity function. The sensitivty function basically show how well your control implementation is able to mitigate disturbanced. So we can see the azimuth offset as a tuning know, When we disregard the azimuth offset, the sensitivity function shows that it is either possible that you reduce external disturbanced, but if you are unlucky, you exaggurate the disturbanced tremendously. This phenomenom is called directionality in your control implementation.
So now when we turn this knob, and select the optimal offset, we can minimize this directionality. So no matter which signal you put in your closed-loop control implementation, you get the same performance, which is a good thing.

## Slide 12: Fatigue load reductions
Introduction Recap MBC Decoupling analysis High-fidelity results
Notes: Now let’s see what happend with the spectra of our pitch and blade root out of moment signals for the case of NO IPC, IPC without the offset, and IPC with the offset. So for no IPC you can see clear peaks in the blade moment spectra for 1P and 2P. When we enable IPC without the offset, we see an attenuation of the 1P peak, but a big exeguration of the 2P peak at a high frequency in both ptch and loads. When we include the azimuth offset, we see nice reduction of both frequencies.

## Slide 13: Damage Equavalent Load reductions
Addition of 2P IPC without offset WORSENS performance
Introduction Recap MBC Decoupling analysis High-fidelity results
Notes: Finally we look at the Damage Equivalent Load, which is a measure for the fatigue loading of the blades. The results are normalized with respect to the No IPC case. So no IPC has a DEL of 1, IPC without offset, clearly worsens the performande, while by including the offset, we can attain a nice benefit in terms of DEL.

## Slide 14: Wrap-up
The correct azimuth offset results in:
Improved decoupling
Diminished sensitivity directionality
Crucial for implementation of 2P IPC
Worsened performance if not implemented
Notes: So as a wrap up. For the implementation of IPC, especially for higher-harmonic reductions, we need the azimuth offset for:
Improved decoupling
Reducing the directionality
Crucial for reduction of a combined 1P + 2P implementation
As IPC would otherwise result in performance detoriation.

## Slide 15: On the Importance of the Azimuth Offset for 2P Individual Pitch Control
[1] Bossanyi E. Individual blade pitch control for load reduction.
[2] Houtzager I, van Wingerden JW, Verhaegen M. Wind turbine load reduction by rejecting the periodic load disturbances.
[3] Mulders S. Iterative feedback tuning of feedforward IPC for two-bladed wind turbines: A comparison with conventional IPC.
[4] Bossanyi EA, Fleming PA, Wright AD. Validation of individual pitch control by field tests on two-and three-bladed wind turbines
spmulders Sebastiaan_Mulders
Sebastiaan Mulders and Jan-Willem van Wingerden
Notes: Thank you