## MS selection
Select member state(s)
Regulations available |  |  | Austria | Denmark | Spain | Germany | Norway | Austria
Reaction to fire
Internal walls/linings | Typical room (15 m2): Walls and Ceiling |  | D-d0/B-s1, d0* | B-s1,d0* | C-s2,d0 | - | - | D-d0/B-s1, d0*
| Typical room (15 m2): Floor |  | Dfl / Cfl-s1* | B-s1,d0* | EFL | - | - | Dfl / Cfl-s1*
| Fire protected escape route: Walls and Ceiling |  | C-s1, d0/A2-s1, d0* | B-s1,d0 | B-s1,d0 | A2-s1, d0* | B-s1,d0 | C-s1, d0/A2-s1, d0*
| Fire protected escape route: Floor |  | Bfl-s1/A2fl-s1* | Dfl-s1 | CFL-s1 | A2fl– s1 | Dfl–s1 | Bfl-s1/A2fl-s1*
External Walls (façade systems) Low-rise building | Height [m] |  | < 7 | - | < 18 | < 7 | - | < 7
| 1st Group | Distance from boundary [m] | - | B-s1,d2 | - | < 2.5 | - | -
|  | External wall RtF classification | D-d1 | B-s1,d2 | C-s3, d0 | C – s1, d0 | - | D-d1
| 2nd Group | Distance from boundary [m] | - | B-s1,d2 | - | > 2.5 | - | -
|  | External wall RtF classification | - | B-s1,d2 | - | E – d0 | - | -
| 3rd Group | Distance from boundary [m] | - | B-s1,d2 | - | - | - | -
|  | External wall RtF classification | - | B-s1,d2 | - | - | - | -
| 4th Group | Distance from boundary [m] | - | B-s1,d2 | - | - | - | -
|  | External wall RtF classification | - | B-s1,d2 | - | - | - | -
External Walls (façade systems) High-rise building | Height [m] |  | > 7 | - | > 18 | < 7 | - | > 7
| 1st Group | Distance from boundary [m] | - | NP | - | - | - | -
|  | External wall RtF classification | B-d1 | NP | B - s3, d0 | A2-s1,d0 | - | B-d1
| 2nd Group | Distance from boundary [m] | - | NP | - | - | - | -
|  | External wall RtF classification | - | NP | - | - | - | -
| 3rd Group | Distance from boundary [m] | - | NP | - | - | - | -
|  | External wall RtF classification | - | NP | - | - | - | -
| 4th Group | Distance from boundary [m] | - | NP | - | - | - | -
|  | External wall RtF classification | - | NP | - | - | - | -
Remark |  |  | * : < 7m / > 7m | * In some cases could D-s2,d2 be accepted | - | *: for > 7m | - | * : < 7m / > 7m
Reference 1 |  |  | OIB2, 2015 | - | - | MBO + MVV TB 2019 | - | OIB2, 2015
Reference 2 |  |  | - | - | - | - | - | -
Reference 3 |  |  | - | - | - | - | - | -
Resistance to fire
Definition of Building Height (Height of Roof/Height to top floor Slab) |  |  | Slab | Slab | Slab | Slab | Storeys | Slab
Group 1: 1-1½ stories above terrain | max. height [m] |  | <7* | <5.1 | <15 | <7* | - | <7*
| Structural frame (beam, column) | No sprinklers | R30*2 | R30 | R90 | R30/R60*2 | R15 | R30*2
|  | Sprinklers | R30 | R30 | R90 | R30 | - | R30
| Load bearing wall | No sprinklers | REI30*2 | R30 | R90 | R30/R60*3 | R15 | REI30*2
|  | Sprinklers | REI30*2 | R30 | R90 | REI30 | - | REI30*2
| Slab (floor) | No sprinklers | - | REI30 | R90 | - | R15 | -
|  | Sprinklers | - | REI30 | R90 | - | - | -
| Fire partition wall | No sprinklers | - | EI60 | - | - | EI30 | -
|  | Sprinklers | - | EI60 | - | - | - | -
| Fire wall (between two ground matrices) | No sprinklers | REI60 | REI60 A2-s1,d0 | - | REI60 | EI30 | REI60
|  | Sprinklers | REI60 | REI60 A2-s1,d0 | - | REI60 | - | REI60
| Fire barrier | No sprinklers | EI30 | - | EI60 | EI30 | EI30 | EI30
|  | Sprinklers | EI30 | - | EI60 | EI30 | - | EI30
| External wall |  | EI30 | REI30/EI30 | - | EI30 | - | EI30
| Demands for Fire comp. size | No sprinklers | - | <150/600 m² | - | - | - | -
|  | Sprinklers | - | 10000 m² | - | - | - | -
Group 2: 2 stories above terrain | max. height [m] |  | <7* | <5.1 | <15 | <7*4 | - | <7*
| Structural frame (beam, column) | No sprinklers | R30*2 | R60 | R90 | R30/R60*2 | R15 | R30*2
|  | Sprinklers | R30 | R60 | R90 | R30 | - | R30
| Load bearing wall | No sprinklers | REI30*2 | R60 | R90 | R30/R60*3 | R15 | REI30*2
|  | Sprinklers | REI30*2 | R60 | R90 | REI30/R30*5 | - | REI30*2
| Slab (floor) | No sprinklers | - | REI60 | R90 | - | R15 | -
|  | Sprinklers | - | REI60 | R90 | - | - | -
| Fire partition wall | No sprinklers | - | EI60 | - | - | EI30 | -
|  | Sprinklers | - | EI60 | - | - | - | -
| Fire wall (between two ground matrices) | No sprinklers | REI60 | REI60 A2-s1,d0 | - | REI60 | EI30 | REI60
|  | Sprinklers | REI60 | REI60 A2-s1,d0 | - | REI60 | - | REI60
| Fire barrier | No sprinklers | EI30 | - | EI60 | EI30 | EI30 | EI30
|  | Sprinklers | EI30 | - | EI60 | EI30 | - | EI30
| External wall |  | EI30 | REI60/EI30 | - | EI30 | 0 | EI30
| Demands for Fire comp. size | No sprinklers | - | <150/600 m² | - | - | - | -
|  | Sprinklers | - | <10000 m² | - | - | - | -
Group 3: 3 stories above terrain | max. height [m] |  | 11*5 | <9.6 m | <15 | <13*6 | - | 11*5
| Structural frame (beam, column) | No sprinklers | R60*6 | R60+ | R90 | R60*7 | - | R60*6
|  | Sprinklers | R60 | R60 | R90 | R60 | - | R60
| Load bearing wall | No sprinklers | R60 | R60+ | R90 | R60 | - | R60
|  | Sprinklers | R60 | R60 | R90 | R60 | - | R60
| Slab (floor) | No sprinklers | REI60 | REI60 | R90 | REI60 | - | REI60
|  | Sprinklers | REI60 | REI60 | R90 | REI60 | - | REI60
| Fire partition wall | No sprinklers | - | EI60 | - | - | - | -
|  | Sprinklers | - | EI60 | - | - | - | -
| Fire wall (between two ground matrices) | No sprinklers | REI60-M | - | - | REI60-M | - | REI60-M
|  | Sprinklers | REI60-M | - | - | REI60-M | - | REI60-M
| Fire barrier | No sprinklers | EI60 | - | EI60 | EI60 | - | EI60
|  | Sprinklers | EI60 | - | EI60 | EI60 | - | EI60
| External wall |  | EI60 | REI60+/EI30 | - | EI60 | - | EI60
| Demands for Fire comp. size | No sprinklers | - | <150/600 m² | - | - | - | -
|  | Sprinklers | - | <10000 m² | - | - | - | -
Group 4: 4 stories above terrain | max. height [m] |  | <22 | <9.6 m | <15 | <13*4*6 | - | <22
| Structural frame (beam, column) | No sprinklers | R90 | R60+ or R60 A2-s1,d0 | R90 | R60*7 | NP | R90
|  | Sprinklers | R90 | R60 | R90 | R60 | R60 | R90
| Load bearing wall | No sprinklers | R90 | R60+ or REI60 A2-s1,d0 | R90 | R60 | NP | R90
|  | Sprinklers | R90 | REI60 | R90 | R60 | R60 | R90
| Slab (floor) | No sprinklers | REI90 | REI60+ | R90 | REI60 | NP | REI90
|  | Sprinklers | REI90 | REI60+ | R90 | REI60 | R60 | REI90
| Fire partition wall | No sprinklers | - | - | - | - | - | -
|  | Sprinklers | - | - | - | - | EI60 | -
| Fire wall (between two ground matrices) | No sprinklers | REI90-M | - | - | REI60-M | - | REI90-M
|  | Sprinklers | REI90-M | - | - | REI60-M | EI60 | REI90-M
| Fire barrier | No sprinklers | EI90 | - | EI60 | EI60 | - | EI90
|  | Sprinklers | EI90 | REI60+/EI60 | - | EI60 | - | EI90
| External wall |  | - | - | - | - | - | -
| Demands for Fire comp. size | No sprinklers | - | <150/600 m² | - | - | - | -
|  | Sprinklers | - | <10000 m² | - | - | - | -
Group 5: 5 stories above terrain | max. height [m] |  | <22 | <12 m | <15* | >13 | - | <22
| Structural frame (beam, column) | No sprinklers | R90 | R60 A2-s1,d0 | R90 | R90 | NP | R90
|  | Sprinklers | R90 | R60 A2-s1,d0 | R90 | R90 | R 90 A2-s1,d0* | R90
| Load bearing wall | No sprinklers | R90 | R60 A2-s1,d0 | R90 | R90 | NP | R90
|  | Sprinklers | R90 | R60 A2-s1,d0 | R90 | R90 | R 60 A2-s1,d0* | R90
| Slab (floor) | No sprinklers | REI90 | R60 A2-s1,d0 | R90 | REI90 | NP | REI90
|  | Sprinklers | REI90 | R60 A2-s1,d0 | R90 | REI90 | R 60 A2-s1,d0* | REI90
| Fire partition wall | No sprinklers | - | R60 A2-s1,d0 | - | - | EI60 A2-s1,d0* | -
|  | Sprinklers | - | R60 A2-s1,d0 | - | - | - | -
| Fire wall (between two ground matrices) | No sprinklers | REI90-M | - | - | REI90-M | EI60 A2-s1,d0* | REI90-M
|  | Sprinklers | REI90-M | - | - | REI90-M | - | REI90-M
| Fire barrier | No sprinklers | EI90 | - | EI60 | EI90 | EI60 A2-s1,d0* | EI90
|  | Sprinklers | EI90 | - | EI60 | EI90 | - | EI90
| External wall |  | EI90 | REI120+/EI60 | - | EI90 | - | EI90
| Demands for Fire comp. size | No sprinklers | - | <150/600 m² | - | - | - | -
|  | Sprinklers | - | <10000 m² | - | - | - | -
Group 6: 6-7 stories above terrain | max. height [m] |  | <22*7 | <22 m | <28 | >13 | - | <22*7
| Structural frame (beam, column) | No sprinklers | R90 | R120 A2-s1,d0 or R120+ | R120 | R90 | NP | R90
|  | Sprinklers | R90 | R120 A2-s1,d0 or R120+ | R120 | R90 | R 90 A2-s1,d0* | R90
| Load bearing wall | No sprinklers | R90 | REI120 A2-s1,d0 or REI120+ | R120 | R90 | NP | R90
|  | Sprinklers | R90 | REI120 A2-s1,d0 or REI120+ | R120 | R90 | R 60 A2-s1,d0* | R90
| Slab (floor) | No sprinklers | REI90 | REI120 A2-s1,d0/ REI60 A2-s1,d0*3 | R120 | REI90 | NP | REI90
|  | Sprinklers | REI90 | REI120 A2-s1,d0/ REI60 A2-s1,d0*3 | R120 | REI90 | R 60 A2-s1,d0* | REI90
| Fire partition wall | No sprinklers | - | EI60 | - | - | EI60 A2-s1,d0* | -
|  | Sprinklers | - | RE60 | - | - | - | -
| Fire wall (between two ground matrices) | No sprinklers | REI90-M | REI120 A2-s1,d0 | - | REI90-M | EI60 A2-s1,d0* | REI90-M
|  | Sprinklers | REI90-M | REI120 A2-s1,d0 | - | REI90-M | - | REI90-M
| Fire barrier | No sprinklers | EI90 | - | EI90 | EI90 | EI60 A2-s1,d0* | EI90
|  | Sprinklers | EI90 | - | EI90 | EI90 | - | EI90
| External wall |  | EI90 | REI120+/EI60 | EI90 | EI90 | - | EI90
| Demands for Fire comp. size | No sprinklers | - | <150/600 m² | - | - | - | -
|  | Sprinklers | - | <10000 m² | - | - | - | -
Group 7: 8 stories above terrain | max. height [m] |  | - | <22 m | <28* | >13 | - | -
| Structural frame (beam, column) | No sprinklers | - | R120 A2-s1,d0 or R120+ | R120 | R90 | NP | -
|  | Sprinklers | - | R120 A2-s1,d0 or R120+ | R120 | R90 | R 90 A2-s1,d0* | -
| Load bearing wall | No sprinklers | - | REI120 A2-s1,d0 or REI120+ | R120 | R90 | NP | -
|  | Sprinklers | - | REI120 A2-s1,d0 or REI120+ | R120 | R90 | R 60 A2-s1,d0* | -
| Slab (floor) | No sprinklers | - | REI120 A2-s1,d0/ REI60 A2-s1,d0*3 | R120 | REI90 | NP | -
|  | Sprinklers | - | REI120 A2-s1,d0/ REI60 A2-s1,d0*3 | R120 | REI90 | R 60 A2-s1,d0* | -
| Fire partition wall | No sprinklers | - | EI60 | - | - | EI60 A2-s1,d0* | -
|  | Sprinklers | - | RE60 | - | - | - | -
| Fire wall (between two ground matrices) | No sprinklers | - | REI120 A2-s1,d0 | - | REI90-M | EI60 A2-s1,d0* | -
|  | Sprinklers | - | REI120 A2-s1,d0 | - | REI90-M | - | -
| Fire barrier | No sprinklers | - | - | EI90 | EI90 | EI60 A2-s1,d0* | -
|  | Sprinklers | - | - | EI90 | EI90 | - | -
| External wall |  | - | REI120+/EI60 | EI90 | EI90 | - | -
| Demands for Fire comp. size | No sprinklers | - | <150/600 m² | - | - | - | -
|  | Sprinklers | - | <10000 m² | - | - | - | -
Group 8: >8 stories above terrain | max. height [m] |  | - | >22 m | >28 | >13 | - | -
| Structural frame (beam, column) | No sprinklers | - | R120 A2-s1,d0 | R180 | R90 | NP | -
|  | Sprinklers | - | R120 A2-s1,d0 | R180 | R90 | R 90 A2-s1,d0* | -
| Load bearing wall | No sprinklers | - | REI120 A2-s1,d0 | R180 | R90 | NP | -
|  | Sprinklers | - | REI120 A2-s1,d0 | R180 | R90 | R 60 A2-s1,d0* | -
| Slab (floor) | No sprinklers | - | REI120 A2-s1,d0/ REI60 A2-s1,d0*3 | R180 | REI90 | NP | -
|  | Sprinklers | - | REI120 A2-s1,d0/ REI60 A2-s1,d0*3 | R180 | REI90 | R 60 A2-s1,d0* | -
| Fire partition wall | No sprinklers | - | REI60 A2-s1,d0 | - | - | EI60 A2-s1,d0* | -
|  | Sprinklers | - | REI60 A2-s1,d0 | - | - | - | -
| Fire wall (between two ground matrices) | No sprinklers | - | REI120 A2-s1,d0 | - | REI90-M | EI60 A2-s1,d0* | -
|  | Sprinklers | - | REI120 A2-s1,d0 | - | REI90-M | - | -
| Fire barrier | No sprinklers | - | NP | EI120 | EI90 | EI60 A2-s1,d0* | -
|  | Sprinklers | - | NP | EI120 | EI90 | - | -
| External wall |  | - | NP | EI120 | EI90 | - | -
| Demands for Fire comp. size | No sprinklers | - | <150/600 m² | - | - | - | -
|  | Sprinklers | - | <10000 m² | - | - | - | -
Reference 1 |  |  | OIB2, 2015 | - | CTE – Código Técnico de la Edificación (Spain) 2015 | MBO + MVV TB 2019 | dibk.no (TEK 17) | OIB2, 2015
Reference 2 |  |  | - | - | - | - | - | -
Reference 3 |  |  | - | - | - | - | - | -
Remark |  |  | * familiy houses, free-standing ≤ 2 units ≤ 400 m² in total *2 only for Basement *3 familiy houses, with sharing the wall with next Building max 3 flat ≤ 400 m² in total *4 for buildings which are not classified in class 1 and 2 *5 ≤ 400 m² for each unit *6 R90 for Basement *7 If the total height for the stories is heigher than the given e.g. 9.6 m, the next group demands must be fullfilled | *1 Single family houses *2 If the total height for the stories is heigher than the given e.g. 9.6 m, the next group demands must be fullfilled *3 If the floor slap is not part of the overall static system R60+ : resistance +60 min protection system R120+ : resistance +60(120) min protection system Sprinklers could in some case reduce fire demands on structures | * If the total height for the stories is heigher than the given e.g. 9.6 m, the next group demands must be fullfilled | * familiy houses, free-standing ≤ 2 units ≤ 400 m² in total *2 Class 2 / Class 3 *3 Pre- scriptive / Performance-based *4 If the total height for the stories is heigher than the given e.g. 9.6 m, the next group demands must be fullfilled *5 familiy houses, with sharing the wall with next Building ≤ 2 units OR > 2 units > 400 m2 in total ≤ 400 m² in total *6 ≤ 400 m² for each unit *7 R90 for Basement | * These are the pre-accepted solutions. Otherwise, you need to document the fire safety and stability of the construction throughout a complete fire course. buildings with ≥3 stories must have an elevator. And buildings with elevator must have sprinkling. | * familiy houses, free-standing ≤ 2 units ≤ 400 m² in total *2 only for Basement *3 familiy houses, with sharing the wall with next Building max 3 flat ≤ 400 m² in total *4 for buildings which are not classified in class 1 and 2 *5 ≤ 400 m² for each unit *6 R90 for Basement *7 If the total height for the stories is heigher than the given e.g. 9.6 m, the next group demands must be fullfilled

## Raw data Reaction to Fire
Interpreting data:
Minimum requirements acc. to legislations are marked with bold (mandatory). According to pre-accepted guidelines is without bold. NP stands for "Not permitted".
Internal Walls / Linings |  | Austria | Belgium | Denmark | France | Germany | Greece | Italy | Norway | Poland | Romania | Spain | Sweden | Switzerland | U.K.
Typical room (15 m2): Walls and Ceiling |  | D-d0/B-s1, d0* | C-s2, d1 | B-s1,d0* |  | - | C-s2,d2 |  |  | B-s1,d0 |  | C-s2,d0 |  | D-s1,d0 | C-s3,d2
Typical room (15 m2): Floor |  | Dfl / Cfl-s1* | CFl-s1 | B-s1,d0* |  | - | Dfl-s2 |  |  | B-s1,d0 |  | EFL |  | Bfl-s1 | -
Fire protected escape route: Walls and Ceiling |  | C-s1, d0/A2-s1, d0* | A2-s1, d1 | B-s1,d0 |  | A2-s1, d0* | A2-s1,d1 |  | B-s1,d0 | A2-s1, d0 |  | B-s1,d0 |  | A2-s1, d0 | B-s3,d2
Fire protected escape route: Floor |  | Bfl-s1/A2fl-s1* | A2Fl-s1 | Dfl-s1 |  | A2fl– s1 | Bfl-s2 |  | Dfl–s1 | A2fl– s1 |  | CFL-s1 |  | A2fl– s1 | -
External Walls (façade systems) |  | Austria | Belgium | Denmark | France | Germany | Greece | Italy | Norway | Poland | Romania | Spain | Sweden | Switzerland | U.K.
Low-rise buildings: Height [m] |  | < 7 | < 25 |  |  | < 7 | < 23 |  |  |  |  | < 18 |  |  | < 18
1st Group | Distance from boundary [m] | - | - | B-s1,d2 |  | < 2.5 | < 3 |  |  |  |  | - |  |  | < 1
| External wall RtF classification | D-d1 | B-s3,d1* | B-s1,d2 |  | C – s1, d0 | B-s1,d1 |  |  |  |  | C-s3, d0 |  |  | B-s3,d2
2nd Group | Distance from boundary [m] |  |  | B-s1,d2 |  | > 2.5 | 3 - 5 | [7 empty] | > 1
| External wall RtF classification |  |  | B-s1,d2 |  | E – d0 | B-s1,d2 | [7 empty] | -
3rd Group | Distance from boundary [m] |  |  | B-s1,d2 |  |  | 5 - 10
| External wall RtF classification |  |  | B-s1,d2 |  |  | C-s2,d2
4th Group | Distance from boundary [m] |  |  | B-s1,d2 |  |  | > 10
| External wall RtF classification |  |  | B-s1,d2 |  |  | D-s2,d2
High-rise buildings: Height [m] |  | > 7 | > 25 |  |  | < 7 | > 23 |  |  |  |  | > 18 |  |  | > 18
1st Group | Distance from boundary [m] |  |  | NP |  |  | < 3 | [7 empty] | A2-s1,d0
| External wall RtF classification | B-d1 | A2-s1,d0 | NP |  | A2-s1,d0 | A2-s1,d0 |  |  |  |  | B - s3, d0 |  |  | A2-s1,d0
2nd Group | Distance from boundary [m] |  |  | NP |  |  | 3 - 5 | [7 empty] | A2-s1,d0
| External wall RtF classification |  |  | NP |  |  | A2-s1,d1 | [7 empty] | A2-s1,d0
3rd Group | Distance from boundary [m] |  |  | NP |  |  | 5 - 10 | [7 empty] | A2-s1,d0
| External wall RtF classification |  |  | NP |  |  | B-s2,d2 | [7 empty] | A2-s1,d0
4th Group | Distance from boundary [m] |  |  | NP |  |  | > 10 | [7 empty] | A2-s1,d0
| External wall RtF classification |  |  | NP |  |  | C-s2,d2 | [7 empty] | A2-s1,d0
Reference 1 |  | OIB2, 2015 | Royal Decree 2012 | - | - | MBO + MVV TB 2019 | PD41, 2018 | - | - | - | - | - | - | BSR 15-15 | Approved document B, 2019
| Link 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | -
| Reference 2 | - | - | - | - | - | - | - | - | - | - | - | - | - | -
| Link 2 | - | - | - | - | - | - | - | - | - | - | - | - | - | -
| Reference 3 | - | - | - | - | - | - | - | - | - | - | - | - | - | -
| Link 3 | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Remark |  | * : < 7m / > 7m | * for building< 10m : C-s3,d1 | * In some cases could D-s2,d2 be accepted |  | *: for > 7m

## Raw data Fire Resistance
Interpreting data:
Minimum requirements acc. to legislations are marked with bold (mandatory). According to pre-accepted guidelines is without bold. NP stands for "Not permitted".
| The requirements |  | Austria | Belgium | Denmark | France | Germany | Greece | Italy | Norway | Poland | Romania | Spain | Sweden | Switserland | U.K. | Remarks
| Definition of Building Height |  | Slab | Slab | Slab | Slab | Slab | Slab |  | Storeys | Slab |  | Slab |  | Roof | Roof?
(Height of Roof/Height to top floor Slab)
| Group 1: Numb. of stories above terrain |  | 1-1½ | 1-1½ | 1-1½*1 | 1-1½ | 1-1½ | 1-1½ | 1-1½ | 1-1½ | 1-1½ | 1-1½ | 1-1½ | 1-1½ | 1-1½ | 1-1½ | *1: Single family house with both stories in the same dwelling
| max. height [m] |  | <7* | <10 | <5.1 | <5* | <7* | < 5 |  |  | <9 |  | <15 |  | <30 | 0 - 5
| Structural frame | No sprinklers | R30*2 | R60 | R30 | R30 | R30/R60*2 | R 30 |  | R15 | R60 |  | R90 |  | R 60 | R 30
| (beam, column) | Sprinklers | R30 | R60 | R30 | R30 | R30 | R 30 |  |  | R60 |  | R90 |  | R60 | R 30
| Load bearing wall | No sprinklers | REI30*2 | REI60 | R30 | R30 | R30/R60*3 | REI 30 |  | R15 | REI60 |  | R90 |  | REI60 | R 30
|  | Sprinklers | REI30*2 | REI60 | R30 | R30 | REI30 | REI 30 |  |  | REI60 |  | R90 |  | REI60 | R 30
| Slab | No sprinklers | - | R60 | REI30 | REI15 | - | REI 30 |  | R15 | REI30 |  | R90 |  | R60 | REI 30
| (Floor) | Sprinklers | - | R60 | REI30 | REI15 | - | REI 30 |  |  | REI30 |  | R90 |  | R60 | REI 30
| Fire partition wall | No sprinklers | - | - | EI60 | - | - | EI 30 |  | EI30 | - |  | - |  | - | REI 30?
| (please add a short definition) | Sprinklers | - | - | EI60 | - | - | EI 30 |  |  | - |  | - |  | - | REI 30?
| Fire wall | No sprinklers | REI60 | REI60 | REI60 A2-s1,d0 | EI30 | REI60 |  |  | EI30 | REI60 |  | - |  | REI60 |  | When the building is close to (within a certain distance e.g. 2.5 m) the neighbor
| between two ground matrices | Sprinklers | REI60 | REI60 | REI60 A2-s1,d0 | EI30 | REI60 |  |  |  | REI60 |  | - |  | REI60
| Fire barrier | No sprinklers | EI30 | EI60 |  | EI15 | EI30 |  |  | EI30 | REI60 |  | EI60 |  | EI30
| (please add a short definition) | Sprinklers | EI30 | EI60 |  | EI15 | EI30 |  |  |  | REI60 |  | EI60 |  | EI30
| External wall | - | EI30 | - | REI30/EI30 | R15 | EI30 | EI 30 |  |  | EI30(o↔i) |  | - |  | EI30 | REI 30
(Façade system)
| Demands for Fire comp. size | No sprinklers |  |  | <150/600 m² | [11 empty] | Demands of sizes for Fire compartments in local regulations
|  | Sprinklers |  |  | 10000 m² | [11 empty] | Demands of sizes for Fire compartments in local regulations
| Group 2: Numb. of stories above terrain |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | Separat compartments/dwellings on each floor level
| max. height (m) |  | <7* | <10 | <5.1 | <10*2 | <7*4 | <15 |  |  | <9 |  | <15 |  | <30 | 5 - 18
| Structural frame | No sprinklers | R30*2 | R60 | R60 | R60 | R30/R60*2 | R 60 |  | R15 | R60 |  | R90 |  | R 60 | R 60
| (beam, column) | Sprinklers | R30 | R60 | R60 | R60 | R30 | R 60 |  |  | R60 |  | R90 |  | R60 | R 60
| Load bearing wall | No sprinklers | REI30*2 | REI60 | R60 | R60 | R30/R60*3 | REI 60 |  | R15 | REI60 |  | R90 |  | REI60 | R 60
|  | Sprinklers | REI30*2 | REI60 | R60 | R60 | REI30/R30*5 | REI 60 |  |  | REI60 |  | R90 |  | REI60 | R 60
| Slab | No sprinklers | - | R60 | REI60 | REI30 | - | REI 60 |  | R15 | REI30 |  | R90 |  | R60 | REI 60
| (Floor) | Sprinklers | - | R60 | REI60 | REI30 | - | REI 60 |  |  | REI30 |  | R90 |  | R60 | REI 60
| Fire partition wall | No sprinklers | - | - | EI60 | EI30 | - | EI 60 |  | EI30 | - |  | - |  | - | REI 60
|  | Sprinklers | - | - | EI60 | EI30 | - | EI 60 |  |  | - |  | - |  | - | REI 60
| Fire wall | No sprinklers | REI60 | REI60 | REI60 A2-s1,d0 | EI60 | REI60 |  |  | EI30 | REI60 |  | - |  | REI60 |  | When the building is close to (within a certain distance e.g. 2.5 m) the neighbor
| between two grond matrices | Sprinklers | REI60 | REI60 | REI60 A2-s1,d0 | EI60 | REI60 |  |  |  | REI60 |  | - |  | REI60
| Fire barrier | No sprinklers | EI30 | EI60 |  | EI30 | EI30 |  |  | EI30 | REI60 |  | EI60 |  | EI30
|  | Sprinklers | EI30 | EI60 |  | EI30 | EI30 |  |  |  | REI60 |  | EI60 |  | EI30
| External wall | - | EI30 | - | REI60/EI30 | R30 | EI30 | EI 60 |  | 0 | EI30(o↔i) |  | - |  | EI30 | REI 60
(Façade system)
| Demands for Fire comp. size | No sprinklers |  |  | <150/600 m² | [11 empty] | Demands of sizes for Fire compartments in local regulations
|  | Sprinklers |  |  | <10000 m² | [11 empty] | Demands of sizes for Fire compartments in local regulations
| Group 3: Numb. of stories above terrain |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | Separat compartments/dwellings on each floor level
| max. height (m) |  | 11*5 | <10* | <9.6 m | <10*2*3 | <13*6 | <15 |  |  | <9* |  | <15 |  | <30 | 5 - 18
| Structural frame | No sprinklers | R60*6 | R60 | R60+ | R60 | R60*7 | R 60 |  |  | R60 |  | R90 |  | R 60 | R 60
| (beam, column) | Sprinklers | R60 | R60 | R60 | R60 | R60 | R 60 |  |  | R60 |  | R90 |  | R60 | R 60
| Load bearing wall | No sprinklers | R60 | REI60 | R60+ | R60 | R60 | REI 60 |  |  | REI60 |  | R90 |  | REI60 | R 60
|  | Sprinklers | R60 | REI60 | R60 | R60 | R60 | REI 60 |  |  | REI60 |  | R90 |  | REI60 | R 60
| Slab | No sprinklers | REI60 | R60 | REI60 | REI30 | REI60 | REI 60 |  |  | REI30 |  | R90 |  | R60 | REI 60
| (Floor) | Sprinklers | REI60 | R60 | REI60 | REI30 | REI60 | REI 60 |  |  | REI30 |  | R90 |  | R60 | REI 60
| Fire partition wall | No sprinklers | - | - | EI60 | EI30 | - | EI 60 |  |  | - |  | - |  | - | REI 60
|  | Sprinklers | - | - | EI60 | EI30 | - | EI 60 |  |  | - |  | - |  | - | REI 60
| Fire wall | No sprinklers | REI60-M | REI60 |  | EI60 | REI60-M |  |  |  | REI60 |  | - |  | REI60 |  | When the building is close to (within a certain distance e.g. 2.5 m) the neighbor
| between two grond matrices | Sprinklers | REI60-M | REI60 |  | EI60 | REI60-M |  |  |  | REI60 |  | - |  | REI60
| Fire barrier | No sprinklers | EI60 | EI60 |  | EI30 | EI60 |  |  |  | REI60 |  | EI60 |  | EI30
|  | Sprinklers | EI60 | EI60 |  | EI30 | EI60 |  |  |  | REI60 |  | EI60 |  | EI30
| External wall | - | EI60 | - | REI60+/EI30 | R30 | EI60 | EI 60 |  |  | EI30(o↔i) |  | - |  | EI30 | REI 60
(Façade system)
| Demands for Fire comp. size | No sprinklers |  |  | <150/600 m² | [11 empty] | Demands of sizes for Fire compartments in local regulations
|  | Sprinklers |  |  | <10000 m² | [11 empty] | Demands of sizes for Fire compartments in local regulations
| Group 4: Numb. of stories above terrain |  | 4 | 4 | 4*2 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | Separat compartments/dwellings on each floor level
| max. height (m) |  | <22 | <25 | <9.6 m | <28*4 | <13*4*6 | <15* |  |  | <12 |  | <15 |  | <30 | 5 - 18
| Structural frame | No sprinklers | R90 | R120 | R60+ or R60 A2-s1,d0 | R90 | R60*7 | R 90 |  | NP | R120 |  | R90 |  | R 60 | R 90
| (beam, column) | Sprinklers | R90 | R120 | R60 | R90 | R60 | R 60 |  | R60 | R120 |  | R90 |  | R60 | R 90
| Load bearing wall | No sprinklers | R90 | REI120 | R60+ or REI60 A2-s1,d0 | R90 | R60 | REI 90 |  | NP | REI120 |  | R90 |  | REI60 | R 90
|  | Sprinklers | R90 | REI120 | REI60 | R90 | R60 | REI 60 |  | R60 | REI120 |  | R90 |  | REI60 | R 90
| Slab | No sprinklers | REI90 | R120 | REI60+ | REI60 | REI60 | REI 90 |  | NP | REI60 |  | R90 |  | R60 | REI 90
| (Floor) | Sprinklers | REI90 | R120 | REI60+ | REI60 | REI60 | REI 60 |  | R60 | REI60 |  | R90 |  | R60 | REI 90
| Non-load bearing wall | No sprinklers |  |  | EI60 | [10 empty] | REI 90
| (Compartment wall) | Sprinklers |  |  | EI60 | [10 empty] | REI 90
| Fire partition wall | No sprinklers | - | - |  | EI60 | - | EI 90 |  |  | - |  | - |  | -
|  | Sprinklers | - | - |  | EI60 | - | EI 60 |  | EI60 | - |  | - |  | -
| Fire wall | No sprinklers | REI90-M | REI120 |  | EI90 | REI60-M |  |  |  | - |  | - |  | REI60 |  | When the building is close to (within a certain distance e.g. 2.5 m) the neighbor
| between two grond matrices | Sprinklers | REI90-M | REI120 |  | EI90 | REI60-M |  |  | EI60 | - |  | - |  | REI60
| Fire barrier | No sprinklers | EI90 | EI60 |  | EI60 | EI60 |  |  |  | EI90 |  | EI60 |  | EI30
|  | Sprinklers | EI90 | EI60 |  | EI60 | EI60 |  |  | EI60 | EI90 |  | EI60 |  | EI30
| External wall | - | EI90 | E60 | REI60+/EI60 | R60 | EI60 | EI 90 |  |  | EI120 |  | - |  | EI30 | REI 90
(Façade system)
| Demands for Fire comp. size | No sprinklers |  |  | <150/600 m² | [11 empty] | Demands of sizes for Fire compartments in local regulations
|  | Sprinklers |  |  | <10000 m² | [11 empty] | Demands of sizes for Fire compartments in local regulations
| Group 5: Numb. of stories above terrain |  | 5 | 5 | 5*2 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | Separat compartments/dwellings on each floor level
| max. height (m) |  | <22 | <25 | <12 m | <28*4 | >13 | <15* |  |  | <25 |  | <15* |  | <30 | 5 - 18
| Structural frame | No sprinklers | R90 | R120 | R60 A2-s1,d0 | R90 | R90 | R 90 |  | NP | R120 |  | R90 |  | R 60 | NP
| (beam, column) | Sprinklers | R90 | R120 | R60 A2-s1,d0 | R90 | R90 | R 60 |  | R 90 A2-s1,d0* | R120 |  | R90 |  | R60 | R 120
| Load bearing wall | No sprinklers | R90 | REI120 | R60 A2-s1,d0 | R90 | R90 | REI 90 |  | NP | REI120 |  | R90 |  | REI60 | NP
|  | Sprinklers | R90 | REI120 | R60 A2-s1,d0 | R90 | R90 | REI 60 |  | R 60 A2-s1,d0* | REI120 |  | R90 |  | REI60 | R 120
| Slab | No sprinklers | REI90 | R120 | R60 A2-s1,d0 | REI60 | REI90 | REI 90 |  | NP | REI60 |  | R90 |  | R60 | NP
| (Floor) | Sprinklers | REI90 | R120 | R60 A2-s1,d0 | REI60 | REI90 | REI 60 |  | R 60 A2-s1,d0* | REI60 |  | R90 |  | R60 | REI 120
| Fire partition wall | No sprinklers | - | - | R60 A2-s1,d0 | EI60 | - | EI 90 |  | EI60 A2-s1,d0* | - |  | - |  | - | NP
|  | Sprinklers | - | - | R60 A2-s1,d0 | EI60 | - | EI 60 |  |  | - |  | - |  | - | REI 120
| Fire wall | No sprinklers | REI90-M | REI120 |  | EI90 | REI90-M |  |  | EI60 A2-s1,d0* | REI120 |  | - |  | REI60 |  | When the building is close to (within a certain distance e.g. 2.5 m) the neighbor
| between two grond matrices | Sprinklers | REI90-M | REI120 |  | EI90 | REI90-M |  |  |  | REI120 |  | - |  | REI60
| Fire barrier | No sprinklers | EI90 | EI60 |  | EI60 | EI90 |  |  | EI60 A2-s1,d0* | EI30 |  | EI60 |  | EI30
|  | Sprinklers | EI90 | EI60 |  | EI60 | EI90 |  |  |  | EI30 |  | EI60 |  | EI30
| External wall | - | EI90 | E60 | REI120+/EI60 | R60 | EI90 | EI 90 |  |  | EI60(o↔i) |  | - |  | EI30 | REI 120
(Façade system)
| Demands for Fire comp. size | No sprinklers |  |  | <150/600 m² | [11 empty] | Demands of sizes for Fire compartments in local regulations
|  | Sprinklers |  |  | <10000 m² | [11 empty] | Demands of sizes for Fire compartments in local regulations
| Group 6: Numb. of stories above terrain |  | 6-7 | 6-7 | 6-7 | 6-7 | 6-7 | 6-7 | 6-7 | 6-7 | 6-7 | 6-7 | 6-7 | 6-7 | 6-7 | 6-7 | Separat compartments/dwellings on each floor level
| max. height (m) |  | <22*7 | <25 | <22 m | <28*4 | >13 | <27 |  |  | <25 |  | <28 |  | <30 | 5 - 18
| Structural frame | No sprinklers | R90 | R120 | R120 A2-s1,d0 or R120+ | R90 | R90 | R 90 |  | NP | R120 |  | R120 |  | R 60
| (beam, column) | Sprinklers | R90 | R120 | R120 A2-s1,d0 or R120+ | R90 | R90 | R 60 |  | R 90 A2-s1,d0* | R120 |  | R120 |  | R60
| Load bearing wall | No sprinklers | R90 | REI120 | REI120 A2-s1,d0 or REI120+ | R90 | R90 | REI 90 |  | NP | REI120 |  | R120 |  | REI60
|  | Sprinklers | R90 | REI120 | REI120 A2-s1,d0 or REI120+ | R90 | R90 | REI 60 |  | R 60 A2-s1,d0* | REI120 |  | R120 |  | REI60
| Slab | No sprinklers | REI90 | R120 | REI120 A2-s1,d0/ REI60 A2-s1,d0*3 | REI60 | REI90 | REI 90 |  | NP | REI60 |  | R120 |  | R60
| (Floor) | Sprinklers | REI90 | R120 | REI120 A2-s1,d0/ REI60 A2-s1,d0*3 | REI60 | REI90 | REI 60 |  | R 60 A2-s1,d0* | REI60 |  | R120 |  | R60
| Fire partition wall | No sprinklers | - | - | EI60 | EI60 | - | EI 90 |  | EI60 A2-s1,d0* | - |  | - |  | -
|  | Sprinklers | - | - | RE60 | EI60 | - | EI 60 |  |  | - |  | - |  | -
| Fire wall | No sprinklers | REI90-M | REI120 | REI120 A2-s1,d0 | EI90 | REI90-M |  |  | EI60 A2-s1,d0* | REI120 |  | - |  | REI60 |  | When the building is close to (within a certain distance e.g. 2.5 m) the neighbor
| between two grond matrices | Sprinklers | REI90-M | REI120 | REI120 A2-s1,d0 | EI90 | REI90-M |  |  |  | REI120 |  | - |  | REI60
| Fire barrier | No sprinklers | EI90 | EI60 |  | EI60 | EI90 |  |  | EI60 A2-s1,d0* | EI30 |  | EI90 |  | EI30
|  | Sprinklers | EI90 | EI60 |  | EI60 | EI90 |  |  |  | EI30 |  | EI90 |  | EI30
| External wall | - | EI90 | E60 | REI120+/EI60 | R60 | EI90 | EI 60 |  |  | EI60(o↔i) |  | EI90 |  | EI30
(Façade system)
| Demands for Fire comp. size | No sprinklers |  |  | <150/600 m² | [11 empty] | Demands of sizes for Fire compartments in local regulations
|  | Sprinklers |  |  | <10000 m² | [11 empty] | Demands of sizes for Fire compartments in local regulations
| Group 7: Numb. of stories above terrain |  | 8 | 8 | 8*2 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | Separat compartments/dwellings on each floor level
| max. height (m) |  |  | <25* | <22 m | <28*4*3 | >13 | <27* |  |  | <25 |  | <28* |  | <30 | 5 - 18
| Structural frame | No sprinklers |  | R120 | R120 A2-s1,d0 or R120+ | R90 | R90 | R 90 |  | NP | R120 |  | R120 |  | R 60
| (beam, column) | Sprinklers |  | R120 | R120 A2-s1,d0 or R120+ | R90 | R90 | R 60 |  | R 90 A2-s1,d0* | R120 |  | R120 |  | R60
| Load bearing wall | No sprinklers |  | REI120 | REI120 A2-s1,d0 or REI120+ | R90 | R90 | REI 90 |  | NP | REI120 |  | R120 |  | REI60
|  | Sprinklers |  | REI120 | REI120 A2-s1,d0 or REI120+ | R90 | R90 | REI 60 |  | R 60 A2-s1,d0* | REI120 |  | R120 |  | REI60
| Slab | No sprinklers |  | R120 | REI120 A2-s1,d0/ REI60 A2-s1,d0*3 | REI60 | REI90 | REI 90 |  | NP | REI60 |  | R120 |  | R60
| (Floor) | Sprinklers |  | R120 | REI120 A2-s1,d0/ REI60 A2-s1,d0*3 | REI60 | REI90 | REI 60 |  | R 60 A2-s1,d0* | REI60 |  | R120 |  | R60
| Fire partition wall | No sprinklers |  | - | EI60 | EI60 | - | EI 90 |  | EI60 A2-s1,d0* | - |  | - |  | -
|  | Sprinklers |  | - | RE60 | EI60 | - | EI 60 |  |  | - |  | - |  | -
| Fire wall | No sprinklers |  | REI120 | REI120 A2-s1,d0 | EI90 | REI90-M |  |  | EI60 A2-s1,d0* | REI120 |  | - |  | REI60 |  | When the building is close to (within a certain distance e.g. 2.5 m) the neighbor
| between two grond matrices | Sprinklers |  | REI120 | REI120 A2-s1,d0 | EI90 | REI90-M |  |  |  | REI120 |  | - |  | REI60
| Fire barrier | No sprinklers |  | EI60 |  | EI60 | EI90 |  |  | EI60 A2-s1,d0* | EI30 |  | EI90 |  | EI30
|  | Sprinklers |  | EI60 |  | EI60 | EI90 |  |  |  | EI30 |  | EI90 |  | EI30
| External wall | - |  | E60 | REI120+/EI60 | R60 | EI90 | EI 60 |  |  | EI60(o↔i) |  | EI90 |  | EI30
(Façade system)
| Demands for Fire comp. size | No sprinklers |  |  | <150/600 m² | [11 empty] | Demands of sizes for Fire compartments in local regulations
|  | Sprinklers |  |  | <10000 m² | [11 empty] | Demands of sizes for Fire compartments in local regulations
| Group 8: Numb. of stories above terrain |  | >8 | >8 | >8 | >8 | >8 | >8 | >8 | >8 | >8 | >8 | >8 | >8 | >8 | >8 | Separat compartments/dwellings on each floor level
| max. height (m) |  |  | <25* | >22 m | >28 | >13 | >27 |  |  | >25 |  | >28 |  | <30 | 5 - 18
| Structural frame | No sprinklers |  | R120 | R120 A2-s1,d0 | R90 | R90 | R 120 |  | NP | R120 |  | R180 |  | R 60
| (beam, column) | Sprinklers |  | R120 | R120 A2-s1,d0 | R90 | R90 | R 60 |  | R 90 A2-s1,d0* | R120 |  | R180 |  | R60
| Load bearing wall | No sprinklers |  | REI120 | REI120 A2-s1,d0 | R90 | R90 | REI 120 |  | NP | REI120 |  | R180 |  | REI60
|  | Sprinklers |  | REI120 | REI120 A2-s1,d0 | R90 | R90 | REI 60 |  | R 60 A2-s1,d0* | REI120 |  | R180 |  | REI60
| Slab | No sprinklers |  | R120 | REI120 A2-s1,d0/ REI60 A2-s1,d0*3 | REI90 | REI90 | REI 120 |  | NP | REI60 |  | R180 |  | R60
| (Floor) | Sprinklers |  | R120 | REI120 A2-s1,d0/ REI60 A2-s1,d0*3 | REI90 | REI90 | REI 60 |  | R 60 A2-s1,d0* | REI60 |  | R180 |  | R60
| Fire partition wall | No sprinklers |  | - | REI60 A2-s1,d0 | EI60 | - | EI 120 |  | EI60 A2-s1,d0* | - |  | - |  | -
|  | Sprinklers |  | - | REI60 A2-s1,d0 | EI60 | - | EI 60 |  |  | - |  | - |  | -
| Fire wall | No sprinklers |  | REI120 | REI120 A2-s1,d0 | EI90 | REI90-M |  |  | EI60 A2-s1,d0* | REI120 |  | - |  | REI60
| between two grond matrices | Sprinklers |  | REI120 | REI120 A2-s1,d0 | EI90 | REI90-M |  |  |  | REI120 |  | - |  | REI60
| Fire barrier | No sprinklers |  | EI60 | NP | EI60 | EI90 |  |  | EI60 A2-s1,d0* | EI30 |  | EI120 |  | EI30
|  | Sprinklers |  | EI60 | NP | EI60 | EI90 |  |  |  | EI30 |  | EI120 |  | EI30
| External wall | - |  | E60 | NP | R90 | EI90 | EI 120 |  |  | EI60(o↔i) |  | EI120 |  | EI30
(Façade system)
| Demands for Fire comp. size | No sprinklers |  |  | <150/600 m² | [11 empty] | Demands of sizes for Fire compartments in local regulations
|  | Sprinklers |  |  | <10000 m² | [11 empty] | Demands of sizes for Fire compartments in local regulations
| Reference 1 |  | OIB2, 2015 | Royal Decree 2012 | - | - | MBO + MVV TB 2019 | PD41, 2018 | - | dibk.no (TEK 17) | - | - | CTE – Código Técnico de la Edificación (Spain) 2015 | - | BSR 15-15 | Approved document B, 2019
| Link 1 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | -
| Reference 2 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | -
| Link 2 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | -
| Reference 3 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | -
| Link 3 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | -
| Remark |  | * familiy houses, free-standing ≤ 2 units ≤ 400 m² in total *2 only for Basement *3 familiy houses, with sharing the wall with next Building max 3 flat ≤ 400 m² in total *4 for buildings which are not classified in class 1 and 2 *5 ≤ 400 m² for each unit *6 R90 for Basement *7 If the total height for the stories is heigher than the given e.g. 9.6 m, the next group demands must be fullfilled | *If the total height for the stories is heigher than the given e.g. 9.6 m, the next group demands must be fullfilled | *1 Single family houses *2 If the total height for the stories is heigher than the given e.g. 9.6 m, the next group demands must be fullfilled *3 If the floor slap is not part of the overall static system R60+ : resistance +60 min protection system R120+ : resistance +60(120) min protection system Sprinklers could in some case reduce fire demands on structures | *1 Single family houses and max 2 flat *2 2 family houses and max 3 flat *3 If the total height for the stories is heigher than the given e.g. 9.6 m, the next group demands must be fullfilled *4 3 family houses, max 7 flat | * familiy houses, free-standing ≤ 2 units ≤ 400 m² in total *2 Class 2 / Class 3 *3 Pre- scriptive / Performance-based *4 If the total height for the stories is heigher than the given e.g. 9.6 m, the next group demands must be fullfilled *5 familiy houses, with sharing the wall with next Building ≤ 2 units OR > 2 units > 400 m2 in total ≤ 400 m² in total *6 ≤ 400 m² for each unit *7 R90 for Basement | * If the total height for the stories is heigher than the given e.g. 9.6 m, the next group demands must be fullfilled |  | * These are the pre-accepted solutions. Otherwise, you need to document the fire safety and stability of the construction throughout a complete fire course. buildings with ≥3 stories must have an elevator. And buildings with elevator must have sprinkling. | * If the total height for the stories is heigher than the given e.g. 9 m, the next group demands must be fullfilled |  | * If the total height for the stories is heigher than the given e.g. 9.6 m, the next group demands must be fullfilled

## Guide to filling in data (hidden)
Inserting data:
All inputs are given in the "Raw data" sheets. When inputs are given, bold text will indicate a requirement that cannot be neglected. According to pre-accepted guidelines is without bold. NP stands for "Not permitted". If no info is available please put a "-" instead. If more references apply, please write in the remarks which reference apply where. To un-lock the protected cells, use the code "BiW". If a need for changing protected cells occurs, please write Cecilie Bech Fejfer at cefe@teknologisk.dk as it might affect the underlying code.