## Slide 1
Alkistis Papetta / Julia Gottschall
Advancing wind resource assessment in complex terrain with scanning lidar measurements
IEA Wind Task 32 online seminar – 2 July 2020

## Slide 2
Standard Wind Resource Assessment (WRA) for complex terrain sites and related challenges  some introduction
How we tackled these challenges in EWiNo  very brief project overview
The developed approach  combining scanning lidar measurements with flow modelling (with results of demonstration campaigns)
Some words on the business case, and conclusions
Outline
What to expect in this seminar

## Slide 3
Standard Wind Resource Assessment (WRA) for complex terrain sites and related challenges  some introduction
How we tackled these challenges in EWiNo  very brief project overview
The developed approach  combining scanning lidar measurements with flow modelling (with results of demonstration campaigns)
Some words on the business case, and conclusions
Outline
What to expect in this seminar
Notes: Comment: This is really the main part that will be presented by Alkistis.

## Slide 4
Standard WRA procedure
According to Technical Guideline (TR) 6 by FGW
on-site data
spatial extrapolation
temporal extrapolation
Components of an energy yield assessment (EYA) – and WRA, respectively – with reference to corresponding sections of TR 6
Notes: How does this work in complex terrain (onshore) cf. offshore

## Slide 5
Standard WRA procedure
According to Technical Guideline (TR) 6 by FGW
Components of an energy yield assessment (EYA) – and WRA, respectively – with reference to corresponding sections of TR 6
 on-site wind measurements and flow model are key components (possibly making the difference)

## Slide 6
Standard WRA procedure
According to Technical Guideline (TR) 6 by FGW
Where do scanning lidar measurements fit in?
…

## Slide 7
Standard WRA procedure
According to Technical Guideline (TR) 6 by FGW
Where do scanning lidar measurements fit in?
As substitute for the more standard on-site wind measurement (must be at least 12 months according to TR 6)
As an additional short-term wind measurement (according to TR 6)
…

## Slide 8
Standard WRA procedure
According to Technical Guideline (TR) 6 by FGW
Where do scanning lidar measurements fit in?
As substitute for the more standard on-site wind measurement (must be at least 12 months according to TR 6)
As an additional short-term wind measurement (according to TR 6)
Where it best improves the WRA (EYA) result… depends essentially on estimated ucertainties and business case

## Slide 9
Entwicklung eines zweistufigen Verfahrens für die Beurteilung von Windstandorten hinsichtlich ihres Windpotenzials nach der EEG-Novelle 2017
(Development of a two-stage procedure for the assessment of wind sites with regard to their wind potential after the EEG [German Renewable Energy Law] amendment 2017)
Overview of joint R&D project EWiNo
Funded by BMWi for project duration 10.2017 – 03.2020
Coordinated by Fraunhofer IWES, with GEO-NET Umweltconsulting GmbH and four associated partners (windwärts, Naturstrom, Energiequelle, ENERTRAG)
Focus on moderately complex (typical German) terrain  some hills, roughness changes, forest, and not too large wind farms

## Slide 10
Overview of joint R&D project EWiNo
Some of the project conclusions
CFD tools more and more gaining ground but not without an on-site measurement
Short-term measurements neither to replace the standard 1-year campaign nor to inform in an early project phase (acceptance, costs)
Scanning lidar technology is of interest but related costs challenge the business case

## Slide 11
Overview of joint R&D project EWiNo
Some of the project conclusions
CFD tools more and more gaining ground but not without an on-site measurement
Short-term measurements neither to replace the standard 1-year campaign nor to inform in an early project phase (acceptance, costs)
Scanning lidar technology is of interest but related costs challenge the business case
More than a compromise: use most cost-efficient scanning lidar approach to maximise value of flow modelling (and with this optimise WRA / EYA result)

## Slide 12
… what this means in terms of uncertainties…

## Slide 13
… what this means in terms of uncertainties…

## Slide 14
Standard Wind Resource Assessment (WRA) for complex terrain sites and related challenges  some introduction
How we tackled these challenges in EWiNo  very brief project overview
The developed approach  combining scanning lidar measurements with flow modelling (with results of demonstration campaigns)
Some words on the business case, and conclusions
Outline
What to expect in this seminar
Notes: Comment: This is really the main part that will be presented by Alkistis.

## Slide 15
WRA
According to TR6
Use additional measurements to evaluate the performance of flow model and minimize uncertainties
!
For complex-terrain sites (orography variations, roughness variations)
Poor representativeness of reference conditions
Increased uncertainty of flow modelling
Notes: When however, we perform WRA, in complex sites, Inaccuracies following the standard wind resource method become more significant. This can be on site due to the poor representativeness of the reference wind conditions. An important amount of the uncertainties though, is due to the increased uncertainties of the flow model on the site for various reasons such as the model input.
What we suggest (and was also done in the past) as a solution to this is the use of additional measurements to evaluate the performance of the flow model
Also uncertainties are increasing in flow modelling as limited resolution of the grid cannot capture all the variations of the terrain. It is more difficult to reach steady state in complex sites due to flow separation. Turbulence models are validated in flat terrain.

## Slide 16
Measured wind speed is the projection on the LoS of the respective beam
Pulsed lidars: simultaneous measurements in multiple “Range gates”
Scanning: 2 degrees of freedom (elevation + azimuth)
Scanning lidar technology
Measuring principle
Notes: The novelty of the method we will present here is the use of scanning lidar technology.. First I need to shortly introduce the basics of a scanning lidar.
Here I assume that most of you know the basics around the measuring principle of profiling lidars which measure a projection of the wind speed on the LoS beams. The main advantage of scanning lidars its is flexible scanning geometries. Having 2 degrees if freedom the user can choose to scan following various paths (random or structured). This technology when combined with standard wind measuring equipment can have two main benefits. Using a reconstruction approach on certain scanning geometries someone can create time series at multiple locations over the site. The second approach is the flow visualization from the snapshots measured by scanning lidar.

## Slide 17
Measured wind speed is the projection on the LoS of the respective beam
Pulsed lidars: simultaneous measurements in multiple “Range gates”
Scanning: 2 degrees of freedom (elevation + azimuth)
Benefit in combination with standard wind measurements:
  Multi-location time series (reconstruction approach)
Scanning lidar technology
Measuring principle
Notes: Here I assume that most of you know the basics around the measuring principle of profiling lidars which measure a projection of the wind speed on the LoS beams. The main advantage of scanning lidars its is flexible scanning geometries. Having 2 degrees if freedom the user can choose to scan following various paths (random or structured). This technology when combined with standard wind measuring equipment can have two main benefits. Using a reconstruction approach on certain scanning geometries someone can create time series at multiple locations over the site. The second approach is the flow visualization from the snapshots measured by scanning lidar.

## Slide 18
Measured wind speed is the projection on the LoS of the respective beam.
Pulsed lidars: Simultaneous measurements in multiple “Range gates”
Scanning: 2 degrees of freedom (elevation + azimuth)
Benefit in combination with standard wind measurements:
  Multi-location time series (reconstruction approach)
  Flow visualization (snapshots)
Scanning lidar technology
Measuring principle
Notes: The novelty of the method we will present here is the use of scanning lidar technology.. First I need to shortly introduce the basics of a scanning lidar.
Here I assume that most of you know the basics around the measuring principle of profiling lidars which measure a projection of the wind speed on the LoS beams. The main advantage of scanning lidars its is flexible scanning geometries. Having 2 degrees if freedom the user can choose to scan following various paths (random or structured). This technology when combined with standard wind measuring equipment has two main functions. Using a reconstruction approach on certain scanning geometries someone can create time series at multiple locations over the site. The second approach is the flow visualization from the snapshots measured by scanning lidar. In this method we focus on the second functionality.

## Slide 19
Virtual scanning lidar method (VSL)
  Create a simulation of the scanning lidar measurements in flow model
Integrating scanning lidar in WRA
Direct comparison of measured and modelled wind fields (stability, terrain effects) by projection.
Notes: Our idea is to provide multi-position measurements to evaluate the performance of flow model by integratind scanning lidar measurements in flow model. The method is called VSL.. As you can see on the right, the procedure consists of three main aspects which I will go through in the following slides.

## Slide 20
Infrastructure:
  Wind flow model (for preselected wind sectors) (microscale)
  On-site 1 year measurements
  Parallel PPI scanning lidar measurements over POI* (few weeks)
Virtual scanning lidar method
* Positions of interest
Notes: Strating from the infrastructure, It is important to note that the method does not replace the minimum requirements by the guidelines, but it rather adds information using scanning lidar measurements.
More precisely the minimum infrastructure to perform this method is a wind flow model, 1 year on site measurements compliant with the guideline rules and last and more important parallel PPI scanning lidar measurements to cover the POI

## Slide 21
Simulated wind field projected on the LOS geometry
Virtual scanning lidar method
Constructing VSL
UTM x [m]
UTM y [m]
Notes: When having the scanning lidar measurements on site someone can construct the digital twin of the scanning lidar

## Slide 22
UTM x [m]
UTM y [m]
Simulated wind field projected on the LOS geometry
  For a reference wind direction:
Virtual scanning lidar method
Constructing VSL
Dir
Notes: Having our infrastructure and specifically the scanning lidar geometry on site we can construct the VSL, by projecting the simulated wind field on the LOS geometry

## Slide 23
UTM x [m]
UTM y [m]
Simulated wind field projected on the LOS geometry
  For a reference wind direction:
    Extract simulated wind vector at LoS locations
Virtual scanning lidar method
Constructing VSL
Dir
Notes: We extract the simulated wind vector at the LoS location

## Slide 24
Simulated wind field projected on the LOS geometry
  For a reference wind direction:
    Extract simulated wind vector at LoS locations
    Project simulated vector on LoS geometry
Virtual scanning lidar method
Constructing VSL
Dir
UTM x [m]
UTM y [m]
UTM y [m]
UTM x [m]
VSL
Notes: And project this vector on the LoS geometry, the result is the VSL.

## Slide 25
Compare VSL and actual scanning lidar measurements
Virtual scanning lidar method
Calibration of flow model
VSL
Scanning lidar
Notes: In the last we can compare the calculates VSL to the actual scanning lidar measurements

## Slide 26
Compare VSL and actual scanning lidar measurements
Identify mismatches (larger than measurement statistical uncertainty)
Virtual scanning lidar method
Calibration of flow model
VSL
Scanning lidar
Notes: BY comparing the two we can identify significant mismatches (errors). Significant here means error that exceed the statistical uncertainty of the measurements

## Slide 27
Compare VSL and actual scanning lidar measurements
Identify mismatches (larger than measurement statistical uncertainty)
Tune flow model (terrain, stability) to reduce disagreement
Virtual scanning lidar method
Calibration of flow model
VSL
Scanning lidar
Notes: Depending on the set up of the flow model these errors can be minimized by tuning the input and the initial conditions of the flow model for a site. As a result we can have a calibrated wind flow model set up for a site

## Slide 28
Two demonstration campaigns during EWiNO project
Sites in Germany:
  Herleshausen (site in Hessen)
  Lügde (site in Nord-Rhine Westphalia)
    Sites with moderately complex terrain
    Pre-construction stage
Simulations by two steady state microscale models:
  FITNAH (GEO-NET)
  FIWind (Fraunhofer IWES)
Demonstration campaigns
  *both models had good performance over the site but here we only show FIWind
Notes: This method was demonstrated during EWiNo project at two sites in Germany. Both sites had moderately complex terrain and were at pre-construction stage. The wind flow simulations on the site were performed usinf two steady state microscale models. The first one is a microscale in house model of GEO-NET

## Slide 29
Galion 4000 – Scanning lidar
Range 0-4 km (along „Line of Sight” [LoS])
Pulsed LiDAR: Simultaneous measurements„Range Gates“
Flexible Geometry (Azimuth, Elevation)
Measured quantity is fraction of the wind speed along beam direction (LoS)
Verified at Fraunhofer IWES premises
Setting up the infrastructure
Scanning lidar
Notes: Fraunhofer IWES infrastructure during these campaigns consisted of a Galion 4000 which was used as the scanning lidar instrument

## Slide 30
Setting up the infrastructure
Model
FIWind : Fraunhofer IWES Wind simulation environment
IWES in-house development: Flow solver based on open source code OpenFOAM with own optimizations for wind energy applications (forest, stratification, complex terrain, ...)
FIWind was validated at different locations in complex terrain (Kassel, NEWA project¹) 
¹Chang, Chi-Yao, et al. "A consistent steady state CFD simulation method for stratified atmospheric boundary layer flows." Journal of Wind Engineering and Industrial Aerodynamics 172 (2018): 55-67
Notes: The FIWIND model was run by Fraunhofer IWES

## Slide 31
Steady state microscale flow model (FIWind)
Input/Intial conditions:
Neutral stratification
36 (Site 1) / 12 (Site 2) directional sectors
25 x 25 m mesh resolution
Terrain maps
Landcover maps
Results
Infrastructure
Model
Notes: Some more details of the infrastructure are shown in this slide. The model run under neutral stratification for all the simulations.

## Slide 32
Results
Infrastructure
Model
Scanning lidar
Steady state microscale flow model (FIWind)
Input/Intial conditions:
Neutral stratification
36 (Site 1) / 12 (Site 2) directional sectors
25 x 25 m mesh resolution
Terrain maps
Landcover maps
Notes: Here you can also see an overview of the scanning lidar set up for Site 1

## Slide 33
Results
Infrastructure
Model
Scanning lidar
Reference instrument
Site 1
Site 2
Profiling lidar
  1 year data (not overlapping with scanning lidar campaign)
SoDAR
  1 month (overlapping with scanning lidar campaign)
Steady state microscale flow model (FIWind)
Input/Intial conditions:
Neutral stratification
36 (Site 1) / 12 (Site 2) directional sectors
25 x 25 m mesh resolution
Terrain maps
Landcover maps
Notes: For reference measuremetns we used a profiling lidar and a sodar. The reason we had two isntruments is because the 1 year data were not overlapping with the scanning lidar campaign and therefore we had to deploy a sodar to run along the scanning lidar measurements

## Slide 34
Results
Infrastructure
Model
Scanning lidar
Reference instrument
Site 1
Site 2
Profiling lidar
  1 year data (overlapping period with scanning lidar campaign)
Steady state microscale flow model (FIWind)
Input/Intial conditions:
Neutral stratification
36 (Site 1) / 12 (Site 2) directional sectors
25 x 25 m mesh resolution
Terrain maps
Landcover maps
Profiling lidar
  1 year data (not overlapping with scanning lidar campaign)
SoDAR
  1 month (overlapping with scanning lidar campaign)
Notes: For site 2 we had a similar set-up with slightly higher elevation angles for the scanning lidar and we only used one reference measurements from a profiling lidar

## Slide 35
Select common cases in the measured wind conditions capture matrix (α: shear exponent, Dir: inflow direction)
30 minute ensembles from reference and scanning lidar measurements
Results
Example single timestamp – Site 2
(α = 0.44 , Dir = 240°)
Notes: I am moving now to some results from the first demonstration site. The VSL method should be used to validate the model for common wind directions and stability. Therefore we select common cases from the measured wind condirions capture matrix. After calculatinf ensembles from th reference and scanning lidar measurements we select a case from a common cell of the capture matrix and we observe first the measured wind conditions. For example for the selected timestamp you can see the wind and direction profile in the lower part of this slide.

## Slide 36
Capture matrix short vs long period
Capture matrix 1 year
Capture matrix 1 month

## Slide 37
Results
VSL vs Scanning lidar
Choose VSL for the sector corresponding to the reference measured direction
Scanning lidar
VSL
Example case for Herleshausen

## Slide 38
Results
VSL vs Scanning lidar
Choose VSL for the sector corresponding to the reference measured direction
Identify deviations larger than measurement uncertainty (discussed later)
Scanning lidar
VSL
Example case for Herleshausen

## Slide 39
Results
VSL vs Scanning lidar
Choose VSL for the sector corresponding to the reference measured direction
Identify deviations larger than measurement uncertainty (discussed later)
  Any big structures still visible in the scanning lidar measurement?
Scanning lidar
VSL
Example case for Herleshausen

## Slide 40
Results
VSL vs Scanning lidar
Choose VSL for the sector corresponding to the reference measured direction
Identify deviations larger than measurement uncertainty (discussed later)
  Any big structures still visible in the scanning lidar measurement? NO
Scanning lidar
VSL
Example case for Herleshausen

## Slide 41
Results
VSL vs Scanning lidar
Choose VSL for the sector corresponding to the reference measured direction
Identify deviations larger than measurement uncertainty (discussed later)
  Any big structures still visible in the scanning lidar measurement? NO
  Terrain / landcover mismatches?
Scanning lidar
VSL
Example case for Herleshausen

## Slide 42
Results
VSL vs Scanning lidar
Choose VSL for the sector corresponding to the reference measured direction
Identify deviations larger than measurement uncertainty (discussed later)
  Any big structures still visible in the scanning lidar measurement? NO
  Terrain / landcover mismatches? YES - Over speeding in front and behind hill (on average 30% over prediction)
Scanning lidar
VSL
Example case for Herleshausen
Notes: Possible reasons for overspeeding:
Roughness maps error, Terrain maps error,

## Slide 43
Results
VSL vs Scanning lidar
Choose VSL for the sector corresponding to the reference measured direction
Identify deviations larger than measurement uncertainty (discussed later)
  Any big structures still visible in the scanning lidar measurement? NO
  Terrain / landcover mismatches? YES - Over speeding in front and behind hill (on average 30% over prediction)
  Atmospheric stability mismatch?
Scanning lidar
VSL
Example case for Herleshausen

## Slide 44
Results
VSL vs Scanning lidar
Choose VSL for the sector corresponding to the reference measured direction
Identify deviations larger than measurement uncertainty (discussed later)
  Any big structures still visible in the scanning lidar measurement? NO
  Terrain / landcover mismatches? YES - Over speeding in front and behind hill (on average 30% over prediction)
  Atmospheric stability mismatch? NO (Equal distribution of contours)
Scanning lidar
VSL
Example case for Herleshausen

## Slide 45
Results
Clustering of cases
Cluster cases with similar wind conditions
Compare cluster’s average with VSL
  Assess errors related to different wind conditions (shear profile)
VSL

## Slide 46
Results
Clustering of cases – Example 240°
Scanning lidar
α = 0.1
α = 0.3
α = 0.5
Averaged clusters for 240° sector at Herleshausen
Notes: Here you can see the clustered scanning lidar measurements for different cells of the capture matric with the same inflow direction. We can already expect some deviations by llokng at the profiles of the three cases

## Slide 47
Results
Clustering of cases – Example 240°
Scanning lidar
α = 0.1
α = 0.3
α = 0.5
VSL
Averaged clusters for 240° sector at Herleshausen

## Slide 48
Results
Clustering of cases – Example 240°
Scanning lidar
α = 0.1
α = 0.3
α = 0.5
VSL
Mismatch in the blind zone increases with α
Include differnet stability classes in the model
Good model performance for POI
Averaged clusters for 240° sector at Herleshausen

## Slide 49
Results
Clustering of cases – Example 240°
Scanning lidar
α = 0.1
α = 0.3
α = 0.5
VSL
Mismatch in the blind zone increases with α
Include differnet stability classes in the model
Good model performance for POI
Averaged clusters for 240° sector at Herleshausen
Give more trust to the wind flow models by giving them a fair evaluation method

## Slide 50
First trust your measurements  Calculate the measurement uncertainty
  Statistical uncertainty
  Mounting uncertainty
  Verification uncertainty – verification based on white-box concept (Figures to the right)
Measurement uncertainty
First we need to understand

## Slide 51
Integrating a single scanning lidar only costs ~1.7 times more than conventional WRA
VSL can be used:
  to evaluate wind flow model performance
  to quantitatively measure model uncertainty at POI
Outlook

## Slide 52
Conclusions (on use and business case)
How many scanning lidars will we see in future WRA campaigns?
Consider…
German onshore market (starting point for EWiNo project)
Costs of technology (how many devices)
Use case / integration with WRA process and flow modelling in particular
Significance of results (in the end, the estimated uncertainties decide)

## Slide 53
Acknowledgements
Partners in EWiNo project
Project partner: GEO-NET Umweltconsulting GmbH
Associated partners:

## Slide 54
Federal Republic of Germany
Federal Ministry for Economic Affairs and Energy
Federal Ministry of Education and Research
European Regional Development Fund (ERDF):
Federal State of Bremen
Senator of Civil Engineering, Environment and Transportation
Senator of Economy, Labor and Ports
Senator of Science, Health and Consumer Protection
Bremerhavener Gesellschaft für Investitionsförderung und Stadtentwicklung mbH
Federal State of Lower Saxony
Free and Hanseatic City of Hamburg
Acknowledgements
Fraunhofer IWES is funded by:

## Slide 55
Your feedback / questions / comments ?