## Sheet 1
TYNDP 2020 - General information on transmission projects | [9 empty] | Needs addressed by the project |  | Expected transfer capacity increase
Project ID | Project Name | Description of the project | Country | Commissioning Year | Status ID 1 : Under Consideration, 2 : In Planning but not permitting, 3 : In permitting, 4 : Under Construction | Is the project cross-border? | Is the project internal? | Is the project on the 4th PCI list? | PCI number | Needs addressed by the project | Explanation by the promoter on how the project addresses the need | Transfer capacity increase A-B (MW) | Transfer capacity increase B-A (MW)
1 | RES in north of Portugal | The main objective of this project consists in introducing the network reinforcements that are needed to allow the connection of new RES generation (hydro with pumping and also wind) that is foreseen in the north of Portugal, where the RES potential is high. The project includes a set of new 400 kV OHL that will form a new axis between V. Minho-R. Pena-Feira (PCI 2.16.3). A new 400 kV OHL Pedralva-Sobrado (PCI 2.16.1) is also included in this cluster, in order to ensure the maintenance of the NTC values between PT and ES that were available prior to the connection of these new power plants. | PT | 2021 | 2 | False | True | TRUE | 2.16.1 and 2.16.3 | Infrastructure to address system adequacy deficiencies and/or mitigate the risk of power failures. Infrastructure to improve system flexibility and stability e.g. improve system or local ramp rate, improve transient stability or RoCoF to meet system Needs. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | Adequacy needs are identified in Portugal mainly due to the expected decommissioning of old power plants along with increasing levels of variable generation. The integration of Hydro power plants with pumping (included in this project) are necessary in order to comply with national adequacy standards Flexibility is the ability of a power system to respond to changes in power demand and generation. Storage facilities such as pumped storage and hydro storage schemes with peak generation are one of the solutions to cope with high power ramps Project for integration of Hydro power plants with pumping | 1400 | 1400
4 | Interconnection Portugal-Spain | In order to reach a complete operational Iberian Electricity Market (MIBEL), and strengthen the Internal Energy Market (IEM), the increase of the interconnection between Spain and Portugal is needed. A new OHL 400kV interconnection between Fontefría (Spain) and Ponte de Lima (Portugal). Internal reinforcements complement the cross border section, such as the axis in Spain between Fontefría and Beariz, in order to be able to connect the crossborder project to the existing network, and in Portugal between Ponte de Lima (previously Viana do Castelo) and Vila Nova de Famalicão (previously Vila doConde). This project was included in the 2013, 2015, 2017 and 2019 PCI list (PCI 2.17). | ES ;PT | 2022 | 3 | True | False | TRUE | 2.17 | Infrastructure to tackle a Need identified by one of the European ITEG indicators referring to the 15% interconnection target for 2030: 1. Reduce the price differential between EU countries to below 2EUR/MWh. 2. Contribute to pushing ratio between nominal transmission capacity and installed RES capacity past 30%. 3. Contribute to pushing ratio between nominal transmission capacity and peak load past 30%. Infrastructure to improve system flexibility and stability e.g. improve system or local ramp rate, improve transient stability or RoCoF to meet system Needs. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment Infrastructure and/or market design to provide balancing flexibility (e.g. international pooling / sharing of reserves, coordinated development of reserve capacity) | IoSN report shows that for the 2040NT scenario the yearly average marginal price difference is higher than the 2€/MWh defined by Interconnection Target Expert Group as threshold for developing new interconnections. In addition, Spanish interconnectors nominal transmission capacity is below 30% of the national peak load and RES capacity The increase of interconnection capacity will be essential to cope with the residual load ramps challenge. The increase of interconnection capacity between countries will allow to exchange the power flows from flexibility sources. TYNDP shows a reduction of RES spillage considering the increase of interconnection capacity. New interconnections with cross border impact can enable the increase of exchange of balancing energy (Welfare savings through exchanging balancing energy and trough imbalance netting). Balancing energy refers to products such as Replacement Reserve (RR), manual and automatic Frequency Regulation Reserve (FRR). | 1900 | 1000
16 | Biscay Gulf | The project consists of 370 km HVDC-VSC link (2 bipoles of 1000 MW each) mainly subsea in the Biscay Gulf, between Gatica (Basque Country, ES) and Cubnezais (Aquitaine, FR). Included in the Madrid Declaration, this project aims at improving the interconnection ES-FR. This project was included in the 2013,2015 and 2017 PCi list (PCI 2.7) | ES ;FR | 2027 | 3 | True | False | TRUE | 2.7 | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to tackle a Need identified by one of the European ITEG indicators referring to the 15% interconnection target for 2030: 1. Reduce the price differential between EU countries to below 2EUR/MWh. 2. Contribute to pushing ratio between nominal transmission capacity and installed RES capacity past 30%. 3. Contribute to pushing ratio between nominal transmission capacity and peak load past 30%. Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | The increase of interconnection capacity will be essential to cope with the residual load ramps challenge. The increase of interconnection capacity between countries will allow to exchange the power flows from flexibility sources. IoSN report shows that for the 2040 time horizon there is need for developing projects in the French-Spanish border. By increasing interconnection capacity on ES-FR border, the project contributes to enhance flow distribution and RES integration, and to increase exchanges between France and the Iberian Peninsula. TYNDP shows a reduction of RES spillage considering the increase of interconnection capacity. | 2200 | 2200
23 | FR-BE: Avelin/Mastaing-Avelgem-Horta HTLS | The project consists in the reconductoring of the existing 80km double-circuit 400kV AC cross-border line between Lille (Avelin/Mastaing, FR) - Avelgem (BE) and onwards to Zomergem (Horta, BE) with High Temperature Low Sag conductors to double its capacity. The main driver is relieving congestion on the French-Belgium border resulting from higher power flows within the CWE area, transporting energy through and to Belgium. Today this axis is occasionally a bottleneck in day-ahead flow-based market coupling. Given the expected increase in power flows, it will become a structural bottleneck. Increasing the interconnection capacity between France and Belgium creates synergies between the export position of France in favorable meteorological conditions and the import position of Belgium with higher flows from south (France) to north (Belgium) appearing more frequently on the French-Belgium border. The reinforcement of the section between Avelgem & Horta is part of the project and needed not only to sustain higher flows from France to Belgium but also to evacuate energy in case of high infeed from offshore wind or import from the UK. | BE ;FR | 2022 | 4 | True | False | FALSE |  | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to address system adequacy deficiencies and/or mitigate the risk of power failures. Infrastructure to tackle a Need identified by one of the European ITEG indicators referring to the 15% interconnection target for 2030: 1. Reduce the price differential between EU countries to below 2EUR/MWh. 2. Contribute to pushing ratio between nominal transmission capacity and installed RES capacity past 30%. 3. Contribute to pushing ratio between nominal transmission capacity and peak load past 30%. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | This project increases the degree of interconnectivity between Belgium and France. The possibility of higher market exchanges between these two bidding zones leads to a higher price convergence in more hours yearly and reduces therefore the price differentials. This is also included as key trigger of the 2030 interconnection criteria. France and Belgium face decreasing figures of installed conventionals due to reduction or phaseout of nuclear and bad market conditions for other conventionals. The interconnector contributes to meet adequacy not only in both countries but also in the entire CWE-region. Based on IOsN report, 15% IC-target requires higher cross border transmission capacity. This project contributes to satisfy this need, provided that the project benefits outweigh its costs. RES integration implies higher flows in the meshed AC-grid and thus increases the need for cross border transmission capacity. This project satisfies this need in a cost-efficient manner. | 1000 | 1000
26 | Reschenpass Interconnector Project | New 220kV interconnector between the substations Nauders (AT) and Glorenza (IT). Due to an update of the list of cross-border projects interconnecting Italy with other Member States within 2020, the 2020 interconnection ratio of Italy has been updated accordingly (from previous value of 9% computed by ENTSO-E in TYNDP 2018 to roughly 8%). As the Interconnection level of 10% will not be reached by 2020, Italy is requested to investigate options of further interconnections. | AT ;IT | 2023 | 4 | True | False | FALSE |  | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment Infrastructure to tackle a Need identified by one of the European ITEG indicators referring to the 15% interconnection target for 2030: 1. Reduce the price differential between EU countries to below 2EUR/MWh. 2. Contribute to pushing ratio between nominal transmission capacity and installed RES capacity past 30%. 3. Contribute to pushing ratio between nominal transmission capacity and peak load past 30%. Infrastructure to address system adequacy deficiencies and/or mitigate the risk of power failures. | This project contributes to lower the price differentials between Italian market zones and Austria This project will improve the integration of italian RES generation This project helps Italy to reach the 15% interconnection target by 2030 This project will contribute to reduce system adequacy deficiencies by increasing transmission capacity. | 300 | 300
28 | Italy-Montenegro | The Italy-Montenegro interconnection project includes a new HVDC subsea cable between Villanova (Italy) and Lastva (Montenegro) and the DC converter stations. The second HVDC module (600 MW) of the Italy-Montenegro interconnection project is strictly correlated with the Transbalkan (project 227) and the Mid Continental East (project 144) corridors, and therefore contributes significantly to enable the usage of an increased transmission capacity between Italy and South-Eastern European Countries (especially Romania and Bulgaria) |  | 2026 | 4 | True | False | FALSE |  | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to address system adequacy deficiencies and/or mitigate the risk of power failures. Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | This project contributes to lowering the price differentials between Italian market zones Italy and Montenegro This project will contribute to reduce system adequacy deficiencies by increasing transmission capacity This project will help to solve important congestions among Italian transmission grid This project will improve the integration of italian RES generation | 600 | 600
29 | Italy-Tunisia | The project consists in a new interconnection between Tunisia and Sicily to be realized through an HVDC submarine cable. The realization of the project is supported by the Italian and Tunisian Governments to increase the interconnection capacity of the Euro-Mediterranean system. Moreover, the project will contribute to reduce, under specific conditions, present and future limitations to the power exchanges on the northern Italian border, with France, Switzerland, Austria and Slovenia, and therefore it will allow to significantly increase the transmission capacity and its exploitation by at least 500 MW on that boundary. | IT ;TN | 2027 | 3 | True | False | TRUE | 3.27 | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to address system adequacy deficiencies and/or mitigate the risk of power failures. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | This project contributes to lowering the price differentials between Italian market zones and Tunisia This project will contribute to reduce system adequacy deficiencies by increasing transmission capacity This project will improve the integration of italian RES generation | 600 | 600
33 | Central Northern Italy | The project consists in the strengthening of interconnection between the northern and the central part of Italy. It will involve the upgrading of existing 220 kV over-head line to 400 kV between Colunga and Calenzano substations as well as the removing of limitations on the existing 220 kV network in Central Italy | IT | 2022 | 2 | False | True | FALSE |  | Infrastructure to improve system flexibility and stability e.g. improve system or local ramp rate, improve transient stability or RoCoF to meet system Needs. Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. | In case of failure of the OHL along the Adriatic or Thyrrenic coast the upgraded lines will improve transient stability. The new line will allow congestion reduction on the North Center-Northern border, in order to transport the foreign import to the local loads and to integrate the southern renewable production. | 400 | 400
35 | CZ Southwest-east corridor | A corridor of internal 400 kV overhead lines inside the Czech Republic connecting existing 420 kV substations between Prestice, Kocin and Mirovka in the southwest-east direction. The project consists of buidling a new AC 400 kV overhead line which connects 420 kV substations Kocin and Mirovka with double circuit line of about 120.5 km length and a nominal transmission capacity of 2x1713 MVA, building a AC 400 kV overhead lines that involves changing of a 400 kV existing single-circuit line to double-circuit line with a nominal capacity of 2x1713 MVA between Kocin and Prestice. | CZ | 2028 | 3 | False | True | TRUE | 3.11.3, 3.11.4 | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. Contribution to the power system's operational flexibility by controlling power flows and optimizing use of existing infrastructure Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | This project helps to decrease the curtailed energy in Germany due to extra market transfers (increase of NTC) on the profile DE - CZ which lead to reduction of marginal price. This project besides the increase of NTC also consists of reinforcement of internal lines and therefore facilitates the future need for cross-border flows. The project contains the upgrade of existing 220 kV lines to 400 kV lines which will reduce infrastructure vulnerability and therefore ensure reliable and secure operation of the grid. The project is aiming at facilitation of the power flows from the RES generation in the northern part of Europe and western part of CZ therefore promotes RES integration. | 500 | 500
36 | Kriegers Flak CGS | The Combined Grid Solution (CGS) is a new AC offshore connection between Denmark and Germany with back to back stations placed in Germany. | DE ;DK | 2020 | 4 | True | False | FALSE |  | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to address system adequacy deficiencies and/or mitigate the risk of power failures. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment Infrastructrure improving voltage stability by offering reactive power controllability of converters by system operator(s) | Project connects two market areas (DKE and DE) with high price differentials between EU countries. The projects contributes both, generation capacity and interconnection capacity to mitigate challenges in the DKE system. The projects enables direct cost-efficient connection of 936 MW offshore wind. The project increases system voltage stability by usage of VSC technology and facilitates independent control of active and reactive power. | 400 | 400
37 | Norway - Germany, NordLink | NordLink: a new HVDC connection between Southern Norway and Northern Germany. Estimated subsea cable length: 514km. Capacity: 1400 MW. | DE ;NO | 2020 | 4 | True | False | TRUE | 1.8.1 |  |  | 1400 | 1400
39 | DKW-DE, step 3 | New double circuit 380kV line from Kassoe (DK) to Audorf (DE). As third phase of the Danish-German agreement to upgrade cross border transfere capacity. The project is labelled by the EC as project of common interes (PCI 1.4.1) | DE ;DK | 2020 | 4 | True | False | FALSE |  | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to address system adequacy deficiencies and/or mitigate the risk of power failures. Infrastructure to improve system flexibility and stability e.g. improve system or local ramp rate, improve transient stability or RoCoF to meet system Needs. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | contributes to reduction of price spread by 2040 facilitates exchange of RES and reserves increases system size, thus facilitates sharing of ancillary service high RES increase expected on both sides of the border - further connection via P167 connecting to low correlated RES area | 720 | 1000
40 | Belgium-Luxembourg-Germany: long-term perspective | An increase of transfer capacity across the BE-LU-DE corridor is envisioned towards the 2030-2040 time horizon. Further studies will determine the appropriate implementation option and timing, taking into account: - the expected evolution on the LU-DE border as presented in project 328 Project motivation: This project increases the degree of interconnectivity between the Belgian - Luxemburg - German corridor. The possibility of higher market exchanges between bidding zones leads to a higher price convergence in more hours of the year and reduces therefore the price differentials. RES integration implies higher flows in the meshed AC-grid and thus increases the need for cross border transmission capacity. This project satisfies this need in a cost-efficient manner. | BE ;DE ;LU | 2035 | 1 | True | False | FALSE |  | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment Infrastructure to tackle a Need identified by one of the European ITEG indicators referring to the 15% interconnection target for 2030: 1. Reduce the price differential between EU countries to below 2EUR/MWh. 2. Contribute to pushing ratio between nominal transmission capacity and installed RES capacity past 30%. 3. Contribute to pushing ratio between nominal transmission capacity and peak load past 30%. | Project increases the degree of interconnectivity between the Belgian - Luxemburg - German corridor and allows higher market exchanges leading to higher price convergence. Also part of the 2030 ITEG targets. RES integration implies higher flows in the meshed AC-grid and thus increases the need for cross border transmission capacity. This project satisfies this need in a cost-efficient manner Project increases the degree of interconnectivity between the Belgian - Luxemburg - German corridor and allows higher market exchanges leading to higher price convergence. Also part of the 2030 ITEG targets. | 500 | 500
47 | Westtirol (AT) - Vöhringen (DE) | This project will increase the current power exchange capacity between Austria and Germany by an upgrade of the existing overhead line Vöhringen (DE) - Westtirol (AT) to 380 kV and the extension of existing and errection of new 380-kV-substations including 380/110-kV-transformers. | AT ;DE | 2027 | 2 | True | False | FALSE |  | Infrastructure to tackle a Need identified by one of the European ITEG indicators referring to the 15% interconnection target for 2030: 1. Reduce the price differential between EU countries to below 2EUR/MWh. 2. Contribute to pushing ratio between nominal transmission capacity and installed RES capacity past 30%. 3. Contribute to pushing ratio between nominal transmission capacity and peak load past 30%. Infrastructure to improve system flexibility and stability e.g. improve system or local ramp rate, improve transient stability or RoCoF to meet system Needs. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | Increase of German interconnection level. Better utilisation of existing and future pump storage power plants by improved transport capacities. Connecting German RES power with pump storages in Austria. | 600 | 600
48 | New SK-HU intercon. - phase 1 | This project will increase the transfer capacity between the Slovak and Hungarian transmission systems, improve security and reliability of operation both transmission systems and support North - South RES power flows in CCE region. Main investments of this project are double circuit AC OHL 400 kV from new Gabcikovo (Slovakia) substation to Gonyu (Hungary) substation, with one circuit connected to the Velky Dur (Slovakia) substation and double circuit AC OHL (preliminary armed only with one circuit on Hungarian side) 400 kV from Rimavska Sobota (Slovakia) substation to Sajoivanka (Hungary) substation. | HU ;SK | 2020 | 4 | True | False | TRUE | 3.16, 3.17 | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to improve system flexibility and stability e.g. improve system or local ramp rate, improve transient stability or RoCoF to meet system Needs. Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | The project decreases the marginal costs difference between HU and SK, based on the market simulation results, so it improves market integration. The project increases system flexibility and stability during maintenance periods in North-Eastern Hungary. The project improves operational security at the SK-HU cross-border profile, as without the project cross-border and loop flows in scenarios could violate fulfillment of N-1 security criterion. The project improves accomodation of the north-south flows caused by new RES connections. | 800 | 1300
62 | Estonia-Latvia 3rd IC | Project nr 62 is a planned third 330 kV interconnection between Estonia and Latvia. The project consists of 3 investments of which nr 386 is the main inter-area investment, AC 330 kV OHL between Kilingi-Nõmme substation in Estonia and Riga CHP2 substations. | EE ;LV | 2020 | 4 | True | False | TRUE | 4.2 |  |  | 600 | 600
78 | South West Cluster | New 400kV substation at Hinkley Point. New 400kV transmission route from Hinkley Point to Seabank. Reconstruction of Bridgewater substation for 400kV operation. Uprate Bridgewater - Melksham to 400kV. | GB | 2024 | 3 | False | True | FALSE |  |  |  | 3200 | 3200
81 | North South Interconnector | A new 400 kV interconnector between Woodland in Ireland and Turleenan in Northern Ireland. | GB ;IE | 2023 | 3 | True | False | TRUE | PCI 2.13.1 | Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to address system adequacy deficiencies and/or mitigate the risk of power failures. | The increased transfer capacity and reduction of system separation risk results in a reduction in must run thermal unit requirements, thus allowing additional renewable generation to be dispatched across the island of Ireland. The project establishes a second interconnector between Ireland and Northern Ireland, effectively eliminating the ongoing risk of system separation, thus allowing an increased transfer capacity. This allows a more efficient generation dispatch across the island, resulting in production cost savings. With only one interconnector between IE and NI, the transfer capacity is limited, to reduce the risk of power failures in the event of the loss of the interconnector. This project resolves the issue by providing security against loss of one interconnector, therefore removing restrictions on cross border energy flows | 950 | 900
82 | RIDP I | The infrastructure development is required to facilitate connection of renewable generation in the North and West of the Island. It will further integrate the Ireland and Northern Ireland transmission systems and provide capacity for substantial demand growth. | GB ;IE | 2030 | 2 | True | False | TRUE | 2.13.2 | Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | This development facilitates the connection of renewable generation in the North and West of the island of Ireland. Existing infrastructure in the area is 110 kV; this 220 kV and 275 kV development provides significant additional capacity to allow the secure connection of renewable generation. | 570 | 570
85 | Integration of RES in Alentejo | The main objective of this project consists in introducing the network reinforcements that are needed to allow the connection of new RES generation (mostly solar but also some wind) that is foreseen for the south region of Portugal, where the solar potential is considerably high. The project includes two new 400 kV OHL that will constitute a new axis between F. Alentejo-Ourique-Tavira substations. It is also included the expansion of the Ourique substation to include the 400 kV voltage level and a new 400KV OHL Alqueva-Divor. | PT | 2023 | 2 | False | True | FALSE |  | Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | TYNDP 2018 and 2020 System Needs study showed high level of congestion in the network resulting from the integration of RES (mainly Solar) congestion in the network in the south of Portugal where the solar potential is considerably high. Project for integration of RES (mainly Solar). | 1000 | 1000
92 | ALEGrO | This project realizes the first interconnection between Belgium (Lixhe) and Germany (Oberzier) as a 100 km HVDC link with a bidirectional rated power of 1.000 MW capacity. Project motivation: This project increases the degree of interconnectivity between the Belgian and German bidding zone. The possibility of higher market exchanges between these two bidding zones leads to a higher price convergence in more hours of the year and reduces therefore the price differentials. Due to the future RES increase in whole CWE, the RES spillage will rise significantly especially beyond 2030. This interconnector project allows a better integration of RES in the entire region and especially in Germany. Belgium and Germany face decreasing figures of installed conventionals especially due to the nuclear phaseout in both countries and bad market conditions for other conventionals. The interconnector contributes to meet adecacy not only in both countries but also in the entire CWE-region. Based on the above, the project also directly contributes to the 2020 interconnection targets. | BE ;DE | 2020 | 4 | True | False | FALSE |  | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to address system adequacy deficiencies and/or mitigate the risk of power failures. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | This project increases the degree of interconnectivity between the Belgian and German bidding zone. The possibility of higher market exchanges between these two bidding zones leads to a higher price convergence in more hours of the year and reduces therefore the price differentials. Belgium and Germany face decreasing figures of installed conventionals especially due to the nuclear phase out in both countries and bad market conditions for other conventionals. The interconnector contributes to meet adequacy not only in both countries but also in the entire CWE-region. Due to the future RES increase in whole CWE the RES spillage will rise significantly especially beyond 2030. This interconnector project allows a better integration of RES in the entire region. | 1000 | 1000
94 | GerPol Improvements | Upgrade of the existing 220 kV double interconnection line between Krajnik and Vierraden to 400 kV together with installation of Phase Shifting Transformers (PST) on the two existing interconnection lines (Krajnik-Vierraden by 50Hertz Transmission GmbH in Vierraden and Mikulowa-Hagenverder by PSE S.A. in Mikulowa) including an upgrade of substations Vierraden, Krajnik and Mikulowa. The new PST in Mikulowa on the 400 KV double line Mikulowa–Hagenwerder were already finally commissioned in June 2016. The first two PST in Vierraden have been commissioned in August 2018. The updated 400 kV double line Krajnik – Vierraden is in operation with one system and these two PST in series. On the German side there is a link to the existing 220 kV lines using two 380/220 kV transformers as an intermediate step. Two further PST will replace these two 380/220 kV transformers after the upgrade of the existing German Uckermark-line to 380 kV. This necessary upgrade of the connecting Uckermark-line is delayed due to the lack of an enforceable building permission. | DE ;PL | 2022 | 4 | True | False | FALSE |  | Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to address system adequacy deficiencies and/or mitigate the risk of power failures. | This project contributes a reduction of unscheduled flows DE-PL, PL-CZ and PL-SK by increasing the controllability of the power flow on the DE-PL border. This project enables the integration of additional RES in the area of western and north-western Poland as well as in the eastern part of Germany. Finalization of the project GerPol Improvements allows to increase cross-border capacity on the Polish-German border and thus allows to exchange more energy. Project contributes to mitigate the risk of adequacy deficiencies in Germany and Poland by connecting areas with different mix of generation. | 500 | 1500
103 | Reinforcements Ring NL phase I | Upgrade of existing 380kV circuits in the Dutch main ring from 2,5 kA to 4 kA. | NL | 2025 | 3 | False | True | FALSE |  | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | Upgrade of the internal grid via this project will help facilitated increase of cross-border exchange capacity between different bidding zones reducing thus the price differentials The upgrade of the internal grid will solve congestions due to new power flow patterns for which the grid was not designed for. Connection of high volumes of RES in the future will create high flows for which the grid was not designed for. Upgrading the grid via this project will help transport power from the generation sites to the load centers | 600 | 600
107 | Celtic Interconnector | Celtic Interconnector will be the first interconnection between Ireland and France. A survey of the route of the HVDC (VSC) link with 700 MW capacity has been done from the southern coast of Ireland to La Martyre (Finistère) in France. Motivation for the project : The CELTIC project will improve security of supply in both Ireland and France. It will facilitate increased electricity trading that will result in increased competition and downward pressure on electricity prices. The CELTIC project will also support the development of renewable sources of energy. | FR ;IE | 2026 | 3 | True | False | TRUE | 1.6 | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to improve system flexibility and stability e.g. improve system or local ramp rate, improve transient stability or RoCoF to meet system Needs. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment Infrastructure to tackle a Need identified by one of the European ITEG indicators referring to the 15% interconnection target for 2030: 1. Reduce the price differential between EU countries to below 2EUR/MWh. 2. Contribute to pushing ratio between nominal transmission capacity and installed RES capacity past 30%. 3. Contribute to pushing ratio between nominal transmission capacity and peak load past 30%. | Figures 2.12 and 2.13 of IoSN Report show that average marginal price difference would be higher than 10€/MWh between France and Ireland in future scenarios if no investment is done, and only between 5 and 10€/MWh with the investment. IoSN Report Chapter 5 (Flexibility aspect, Transient and voltage stability related aspects): the ramp increases from NT2025 to NT2040. The project allows Ireland to take benefits from the more stable continental grid, participates in reactive power management and frequency management by quickly changing its active power. IoSN report 2020, figures 2.8-2.11: main drivers of NT scenarios are better access to RES generation (avoiding curtailment) which replaces expensive thermal generation. Figures 2.2-2.3: in Ireland, curtailment decreases by half with the IoSN SEW needs in 2030 compared to 2020. Same for 2040 compared to 2025. Based on IoSN report, 15% IC-target requires higher cross border transmission capacity. This project P107 contributes to satisfy this need (especially for Ireland, by increasing the transmission capacity while the installed RES generation is going higher too). | 700 | 700
110 | Norway-Great Britain, North Sea Link | North Sea Link is a 720 km long subsea interconnector between Norway and Great Britain which is planned to be commissioned in 2021. When realised, it will be the world's longest subsea Interconnector. The main driver for the project is to integrate the hydro-based Norwegian system with the thermal, nuclear and wind-based British system. The interconnector will improve security of supply both in Norway in dry years and in Great Britain in periods with negative power balance (low wind, high demand etc.). In addition, the interconnector will be positive for the European market integration, whilst also facilitating renewable energy in preparation for a power system with lower CO2-emissions. The interconnector is planned to be a 515 kV 1400 MW HVDC subsea interconnector between western Norway (Kvilldal) and eastern England (Blyth). | GB ;NO | 2021 | 4 | True | False | TRUE | 1.10.1 |  |  | 1400 | 1400
111 | 3rd AC Finland-Sweden north | Third AC 400 kV overhead line interconnector between Finland north and Sweden SE1. Strengthening the AC connection between Finland and Sweden is necessary due to market needs, security of supply in Finland, new wind power generation and larger conventional units. | FI ;SE | 2025 | 3 | True | False | FALSE |  | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to address system adequacy deficiencies and/or mitigate the risk of power failures. Infrastructure to tackle a Need identified by one of the European ITEG indicators referring to the 15% interconnection target for 2030: 1. Reduce the price differential between EU countries to below 2EUR/MWh. 2. Contribute to pushing ratio between nominal transmission capacity and installed RES capacity past 30%. 3. Contribute to pushing ratio between nominal transmission capacity and peak load past 30%. Infrastructure to improve system flexibility and stability e.g. improve system or local ramp rate, improve transient stability or RoCoF to meet system Needs. |  | 900 | 800
120 | MOG II: connection of up to 2 GW additional offshore wind Belgium | Following the concept of MOG (project 75), the MOG II aims at centralizing the offshore wind farms in an offshore hub and transporting it via 220 kV AC cables to a substation along a new corridor Stevin-Avelgem (see project 329). The number of hubs is subject to further studies - whereas current working hypothesis indicate 2 or 3 platforms and cable sets. Structure, capacity, timing etc. are all subject to the identification of new offshore concession zones in the Belgian part of the North Sea and subsequent proces to translate this into an implementation plan with all involved stakeholders. Project motivation: Project consists of offshore grid investments that allows to connect the new wave of offshore energy to the mainland(on top of scheduled 2,3GW) in an efficient & reliable way - hence strongly facilitates RES integration for Belgium. A Belgian law has been approved on 4th of April 2019 (DOC 54 3581/008) creating a legal framework for a second Modular Offshore Grid. | BE | 2028 | 2 | False | True | FALSE |  | Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | Project consists of offshore grid investments that allows to connect a new wave of offshore energy to the mainland (on top of the scheduled 2,3GW) in an efficient and reliable way - hence strongly facilitates RES integration for Belgium. | 2000 | 2000
121 | Nautilus: multi-purpose interconnector Belgium - UK | This project considers the possibility of a multi-purpose HVDC interconnection between GB and Belgium, that combines the benefits of connecting electricity markets and offshore wind generation in GB and Belgium. The capacity of the interconnection is still under review, but is likely to be in the range of 1 GW – 2GW, with the reference NTC contribution remaining 1,4GW at this stage. Project motivation: Increasing commercial market exchange capacity between Belgian and GB bidding zones will increase overall EU social welfare. An important security of supply contribution is also achieved through implementation of this project, both from avoided alternative investments as from a reduction in loss of load expectancy. Such adequacy contribution can be linked to the decreasing figures of installed conventionals and increasing RES. Finally, significant benefits related to integration of XB redispatching, balancing markets, and exchange or sharing of ancillary services (frequency coupling, frequency reserves, blackstart, reactive power) across the HVDC-IC between synchronous areas can be obtained. Considering the above, the project therefore also contributes directly to the 2030 interconnection criteria. Additionally, integrating offshore wind capacity on to the interconnector could lead to increased benefits and/or investment savings. | BE ;GB | 2028 | 1 | True | False | FALSE |  | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to address system adequacy deficiencies and/or mitigate the risk of power failures. Infrastructure to improve system flexibility and stability e.g. improve system or local ramp rate, improve transient stability or RoCoF to meet system Needs. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | This project increases the degree of interconnectivity between the Belgian and UK bidding zone and possibility of higher market exchanges which leads to higher price convergence. This is also a key trigger of the 2030 ITEG targets. This project has an important adequacy contribution due to decreasing figures of installed conventionals and increasing RES. This is also a key trigger of the 2030 ITEG targets. This interconnector project between Belgium and UK is designed as a HVDC-link. The full controllability of the HVDC link facilitates the balancing of active and reactive power in the Belgian and UK grid. RES integration implies higher flows within & between AC-grid(s) and thus increases the need for cross border transmission capacity. This project satisfies this need in a cost-efficient manner. This is also a key trigger of the 2030 ITEG targets. | 1400 | 1400
123 | LitPol Link Stage 2 | Construction of new 400 kV AC double-circuit OHL line with a length of 108 km and capacity of 2x1870 MVA between Ostrołęka and Stanisławów. Temporary one circuit will use part of the existing 220 kV single-circuit line between Ostrołęka and Miłosna. In one circuit of 400 kV line, the Wyszków substation will be constructed. After the construction of 400 kV line, the 220 kV line will be disconnected. Extension of 400 kV Ostrołęka and Stanisławów substations for connection of new Ostrołęka - Stanisławów line. | LT ;PL | 2023 | 4 | False | True | TRUE | 4.5.2 |  |  | 500 | 500
124 | NordBalt phase 2 | Second phase includes the internal network reinforcement in Sweden, a key investment to accomplish full utilization of the NordBalt cable between Lithuania and Sweden. The rest of internal investments already commissioned. | LT ;LV ;SE | 2026 | 3 | True | False | TRUE | 4.4 |  |  | 0 | 0
126 | SE North-south short-term reinforcements | Reactive measures in substations and series compensations in order to increase capacity between SE2 and SE3. Replacement of ageing overhead lines that also will contribute to the increased capacity. | SE | 2030 | 2 | False | True | FALSE |  |  |  | 2000 | 2000
127 | Central Southern Italy | The project consists in the reinforcement of southern Italy 400 kV network through new 400 kV lines. The activities will involve the network portions between the substation of Villanova and Foggia, Deliceto and Bisaccia as well as Laino and Altomonte | IT | 2024 | 3 | False | True | FALSE |  | Infrastructure to improve system flexibility and stability e.g. improve system or local ramp rate, improve transient stability or RoCoF to meet system Needs. Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | In case of failure of the first OHL Foggia-Villanova the new line will improve transient stability. The new line will allow congestion reduction in the Southern-Northern border, and the integration of the local renewable production. Reduction of expected RES curtailment | 1000 | 1000
130 | HVDC SuedOstLink Wolmirstedt to area Isar | 2 GW HVDC-connection from North-East Germany (Area of Wolmirstedt), an area with high installed capacities of RES, to the South of Bavaria (area of Isar), an area with high consumption and connections to storage capabilities. A Capacity extension to 4 GW is under investigation. | DE | 2025 | 3 | False | True | TRUE | 3.12 | Infrastructure to improve system flexibility and stability e.g. improve system or local ramp rate, improve transient stability or RoCoF to meet system Needs. Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | Infrastructure improves system flexibility and stability. Controllable HVDC connections stabilize the increasingly stressed German system. DC power lines can provide better controllability in the power grid and support especially voltage stability in the system, as the converters can provide both capacitive and inductive reactive power. In situations with high wind infeed or high pan-European market driven flows, unscheduled load flows from North of Germany over Poland and Czech Republic to Bavaria or Austria can occur. The project will reduce unintended load flows significantly and will relieve the transmission grids of neighboring countries. The project will connect the North-East of Germany, a region with a high amont of renewables covering the annual total energy consumption of the area, with Bavaria, a region with high consumption and structural import need as well as access to large hydro storage capabilities in Alps. | 400 150 100 2000 | 400 150 100 2000
132 | HVDC Line A-North | Project 132 consists of two new HVDC cable from Emden-East to Osterath. The HVDC has a transfer capacity of 2 GW. The project is a grid expansion project for low-loss transmission of high power over long distances from Northern Germany to the Rhineland. Northern Germany is characterized by a large number of regenerative onshore and offshore energy sources which exceed the demand of Northern German loads. The Rhineland, however, is a high-production region with large conventional generation capacity that has to be substituted by renewable generation capacity due to the German coal phase-out. | DE | 2025 | 3 | False | True | FALSE |  | Infrastructure to improve system flexibility and stability e.g. improve system or local ramp rate, improve transient stability or RoCoF to meet system Needs. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment Infrastructrure improving voltage stability by offering reactive power controllability of converters by system operator(s) | The project contributes significantly to security of supply and grid stability through the widespread integration of renewable energies in northern Germany. In particular, the system flexibility is increased by the use of HVDC converter. The project enables the integration of offshore wind energy and prevents potential bottlenecks in the adjacent 380/220 kV grid. With long-range energy transport, the use of DC technology reduces the reactive power demand considerably. For this purpose, the HVDC converters additionally provide reactive power. This helps P132 to comply with the AC voltage bands and thus makes an important contribution to the voltage stability. | 2000 | 2000
138 | Black Sea Corridor | The project consists of one 400kV double circuit OHL Cernavoda-Stalpu with in/out connection of one circuit in Gura Ialomitei, one 400 kV double circuit OHL Smardan-Gutinas in Romania and also the new 400 kV OHL Dobrujda-Burgas in Bulgaria. This project allows transfer of generation from Western cost of the Black Sea towards consumption and storage centers in Central Europe and South-Eastern Europe. | BG ;RO | 2024 | 3 | False | True | TRUE | 3.8 | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to tackle a Need identified by one of the European ITEG indicators referring to the 15% interconnection target for 2030: 1. Reduce the price differential between EU countries to below 2EUR/MWh. 2. Contribute to pushing ratio between nominal transmission capacity and installed RES capacity past 30%. 3. Contribute to pushing ratio between nominal transmission capacity and peak load past 30%. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | Increased cross-border capacities allow European countries to exchange more energy and this will have an impact on reducing the marginal costs. The project contributes to the increase of the transfer capacity across the border between Bulgaria and Romania. The project contributes to reach the 15% interconnection target for 2030 and also will help to reduce the price differentials between the countries. Increase of transfer capacity in the predominant North-South direction at the boundary between Romania and Bulgaria, will support the large scale integration of new RES in the area of Black Sea coast, in both countries and especially Romania. | 600 | 600
142 | CSE4 | The project concerns the construction of a new AC 400kV interconnection between Bulgaria and Greece and new AC 400kV overhead lines at the south part of Bulgaria. This project will increase cross border transfer capacity between Bulgaria and Greece | BG ;GR | 2023 | 4 | True | False | TRUE | 3.7.1, 3.7.2, 3.7.3 and 3.7.4 | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | The project contributes in reducing price differentials indicated in the south part of the region by providing access to more competitive generation sources located in the northeast part. The project will allow further RES integration in northeast part of Greece and in northeast and south Bulgaria. | 930 | 600
144 | Mid Continental East corridor | The project consists of one double circuit 400 kV interconnection line between Serbia and Romania and reinforcement of the network along the western border in Romania: one new simple circuit 400 kV line from Portile de Fier to Resita and upgrade from 220 kV double circuit to 400 kV double circuit of the axis between Resita and Arad, including upgrade to 400 kV of three substations along this path: Resita, Timisoara, Sacalaz. The main aim of this project is increasing the transmission capacity along the East-West corridor in the South-Eastern and Central Europe, simultaneously contributing to the market integration in the region of interest and enhancing the integration of large renewable sources in the Banat region, located in the close proximity of the Serbian-Romanian border. Along with that, the commissioning of the project will strongly improve the security of supply in the mentioned area, thus fulfilling one of the primary postulates of the modern transmission systems' reliable operation. | RO ;RS | 2025 | 3 | True | False | TRUE | 3.22 | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to tackle a Need identified by one of the European ITEG indicators referring to the 15% interconnection target for 2030: 1. Reduce the price differential between EU countries to below 2EUR/MWh. 2. Contribute to pushing ratio between nominal transmission capacity and installed RES capacity past 30%. 3. Contribute to pushing ratio between nominal transmission capacity and peak load past 30%. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | The project contributes to the increase of the transfer capacity across the border between Serbia and Romania. Increased cross-border capacities allow countries to exchange more energy and this will have an impact on reducing the marginal costs. The project contributes to reach the 15% interconnection target for 2030 and also will help to reduce the price differentials between the countries. The project enhances the transmission capacity along the East-West corridor in the South-Eastern and Central Europe. The project supports the large scale integration of new RES in the region of South-West Romania and North-East Serbia. | 617 844 | 335 600
150 | Italy-Slovenia | The project consists in a new HVDC link between Salgareda (Italy) and Divaca/Bericevo (Slovenia) which will strengthen the connection between Slovenia and Italy. On Italian side the project is under permitting since 2012, on Slovenian side the project is under consideration (under study). Terna and ELES are evaluating the opportunity to implement the project according to the following two phases: • reinforcement of existing grid (PSTs, upgrade of existing lines) o Delta GTC contribution: 400 MW • HVDC link (two separate investments: one for the IT side and one for the SI side) o Rated power: 800/600 MW o Commissioning date: 2028 (or later, depending on the Study Phase results in Slovenia) o Delta GTC contribution: 600 MW Due to an update of the list of cross-border projects interconnecting Italy with other Member States within 2020, the 2020 interconnection ratio of Italy has been updated accordingly (from previous value of 9% computed by ENTSO-E in TYNDP 2018 to roughly 8%). As the Interconnection level of 10% will not be reached by 2020, Italy is requested to investigate options of further interconnections. | IT ;SI | 2028 | 3 | True | False | TRUE | 3.21 | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to tackle a Need identified by one of the European ITEG indicators referring to the 15% interconnection target for 2030: 1. Reduce the price differential between EU countries to below 2EUR/MWh. 2. Contribute to pushing ratio between nominal transmission capacity and installed RES capacity past 30%. 3. Contribute to pushing ratio between nominal transmission capacity and peak load past 30%. Infrastructure to improve system flexibility and stability e.g. improve system or local ramp rate, improve transient stability or RoCoF to meet system Needs. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | This project contributes to lowering the price differentials between Italian market zones and Slovenia This project helps Italy to reach the 15% interconnection target by 2030 This project will contribute to overcome flexibility/stability problems due to scarcely meshed grid This project will improve the integration of Italian RES generation | 1000 | 1000
153 | France-Alderney-Britain | France-Alderney-Britain (FAB) is a new HVDC subsea interconnector between Exeter (UK) and Menuel (France) with 1,4 GW capacity. Motivation for the project : The project has two main objectives. The first one is to increase the interconnection capacity between France and Great Britain, to answer the market needs. The second objective is to integrate additional RES generation : Wind generation in Great Britain and the project is also designed to provide a route to connect future marine renewable energy planned to be constructed in the seas around Alderney. This could form part of future offshore meshed grids (e.g. North Sea Offshore Grid) and operate with multi-terminal capability. | FR ;GB | 2025 | 3 | True | False | TRUE | 1.7.1 | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to address system adequacy deficiencies and/or mitigate the risk of power failures. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment Infrastructure to tackle a Need identified by one of the European ITEG indicators referring to the 15% interconnection target for 2030: 1. Reduce the price differential between EU countries to below 2EUR/MWh. 2. Contribute to pushing ratio between nominal transmission capacity and installed RES capacity past 30%. 3. Contribute to pushing ratio between nominal transmission capacity and peak load past 30%. | FAB Link will provide cross border capacity facilitating further access between French and GB markets thereby converging GB and French prices. The GB and French generation mixes are fundamentally different and both are forecast to undergo significant change over the assessment period. FAB Link will provide further capacity between these two markets enhancing security of supply and reducing the risk of power failures. With increasing levels of RES forecast for both France and GB, FAB Link will support the integration and provide these generators access to wider markets thereby reducing the chance of curtailing these carbonised sources of power. FABLink will further contibute to the GB 15% interconnection target and support reducing price differentials. | 1400 | 1400
167 | Viking DKW-GB | 2x700 MW HVDC subsea link across the North Seas. New substations on both sides; Bicker Fen (GB); Revsing (DK) | DK ;GB | 2023 | 4 | True | False | TRUE | 1.14 | Infrastructure to address system adequacy deficiencies and/or mitigate the risk of power failures. Infrastructure to tackle a Need identified by one of the European ITEG indicators referring to the 15% interconnection target for 2030: 1. Reduce the price differential between EU countries to below 2EUR/MWh. 2. Contribute to pushing ratio between nominal transmission capacity and installed RES capacity past 30%. 3. Contribute to pushing ratio between nominal transmission capacity and peak load past 30%. Infrastructure to improve system flexibility and stability e.g. improve system or local ramp rate, improve transient stability or RoCoF to meet system Needs. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | facilitates exchange of RES and reserves project connects two market areas Uses VSC technology, facilitating independent control of active and reactive power connects two low correlated wind areas | 1400 | 1400
170 | Baltic States Synchronization with Continental Europe | Goal of the project is to prepare Baltic states electrical networks for synchronous operation with Continenatal Europe. This project covers a lot of new investments for internal grid reinforcements - new 330 kV and 400 kV AC lines, voltage stabiliser units, synchronous compensators, upgrades of PSS in power stations, internal 110 kV network reinforcement required for synchronization and separation of 110 kV Baltic grid from IPS/UPS system, additional studies. As part of the project, after the synchronization, a new HVDC connection will be established between LT-PL (investment No. 1034) allowing for a commercial exchange of the Baltic States with Continental Europe in the amount of 700 MW. | EE ;LT ;LV ;PL | 2025 | 4 | True | False | TRUE | 4.8 | Infrastructure to allow by 2025 for the synchronisation of the Baltic States with the rest of the EU network Infrastructure to improve system flexibility and stability e.g. improve system or local ramp rate, improve transient stability or RoCoF to meet system Needs. Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to address system adequacy deficiencies and/or mitigate the risk of power failures. | New 700 MW HVDC interconnector "Harmony Link" between Lithuania and Poland, upgrades in Alytus (LT) substation, other internal network strenghtening in Poland, Lithuania, Latvia and Estonia will enable to establish synchronous operation of Baltics States with EU network. New investments HVDC Harmony Link, common Baltic Frequency Stability Assessment System (FSAS), upgrading of monitoring and control systems, new voltage stabiliser units, new synchronous condensers will improve transient and frequency stability in Baltic States. New 700 MW HVDC Harmony Link will be used for trading between Baltic States and this will reduce price differentials between Baltic States and EU. New 700 MW HVDC Harmony Link will increase system adequacy in Baltic Staes, will mitigate risk of power failures and has black start capabilities. | 500 | 1000
172 | ElecLink | ElecLink is a new FR – UK interconnection cable with 1000 MW capacity through the Channel Tunnel between Sellindge (UK) and Mandarins (FR). Converter stations will be located on Eurotunnel concession at Folkestone and Coquelles. This HVDC interconnection is a PCI project (Project of Common Interest) no. 1.7.3 | FR ;GB | 2021 | 4 | True | False | TRUE | 1.7.3 |  |  | 1000 | 1000
173 | FR-BE: PSTs Aubange-Moulaine | Installation of two phase shifting transformers in Aubange, one on each of the 225kV circuits of the Aubange-Moulaine interconnector. Project motivation: The main driver is relieving congestion on the French-Belgium border resulting from higher bulk power flows within the CWE area, transporting energy through and to Belgium. The 225kV axis between Aubange and Moulaine is electrically speaking highly influenced by both France - Belgium and France - Germany cross border flows. Today this axis is occasionally a bottleneck in day-ahead flow-based market coupling. Given the expected increase in power flows, it will become a structural bottleneck. Solving this bottleneck is complementary to project 23 (HTLS upgrade Avelin/Mastaign - Horta) in developing the potential for additional market exchange capacity on the FR-BE border.The investment in PSTs continues to build upon the investment done in 2009/2010 when a second circuit has been installed, as it allows to continue to use the capacity of this 225kV axis in an efficient way. | BE ;FR | 2021 | 4 | True | False | FALSE |  | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to tackle a Need identified by one of the European ITEG indicators referring to the 15% interconnection target for 2030: 1. Reduce the price differential between EU countries to below 2EUR/MWh. 2. Contribute to pushing ratio between nominal transmission capacity and installed RES capacity past 30%. 3. Contribute to pushing ratio between nominal transmission capacity and peak load past 30%. Contribution to the power system's operational flexibility by controlling power flows and optimizing use of existing infrastructure Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | This project increases the degree of interconnectivity between Belgium and France. The possibility of higher market exchanges between these two bidding zones leads to a higher price convergence in more hours yearly and reduces therefore the price differentials. This is also included as key trigger of the 2030 interconnection criteria. Based on IOsN report, 15% IC-target requires higher cross border transmission capacity. This project contributes to satisfy this need, provided that the project benefits outweigh its costs. These PSTs will help to balance the flows over the different cross border lines of the French Belgian interconnector. RES integration implies higher flows in the meshed AC-grid and thus increases the need for cross border transmission capacity. This project satisfies this need in a cost-efficient manner. | 500 | 500
174 | Greenconnector | Greenconnector is an HVDC interconnector project between Italy and Switzerland for power transport using DC cables rather than overhead lines. The route length is about 165 km. The design power is 1000 MW (1200 MW in overload condition), while the DC voltage is +/- 400 kV DC. Two cables will be installed, working with a bipolar scheme. Great part of the cables route will exploit a section of an existing oil pipeline, no longer in service since January 1997. This pipeline crosses the Italian and Switzerland border at Splügenpass and is running close by the two end stations of the Greenconnector project (Bonaduz in Graubunden Canton and Verderio Inferiore, Lecco). The cables will be pulled inside the pipeline itself, reducing the amount of civil works required before and after cable laying and therefore limiting even temporary environmental impact. For about 47 km the cables will run across the Como lake. The selected technology and voltage level make it possible to build a very efficient interconnector with very low losses. | CH ;IT | 2024 | 3 | True | False | TRUE | 2.14 |  |  | 1000 | 1000
176 | Hansa PowerBridge I | New HVDC interconnector between Sweden (SE4) and Germany (50 Hertz, Continental) aiming to enhance the integration of the Nordic and the continental power market. Moreover the interconnector facilitates RES integration and increases the system adequacy in both systems. | DE ;SE | 2026 | 3 | True | False | FALSE |  | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to address system adequacy deficiencies and/or mitigate the risk of power failures. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | The main driver is market integration of the Nordic hydro/nuclear/RES dominated system with the German thermal/RES based system. The infrastructure will reduce price differentials between EU countries. The system adequacy is enhanced in Germany which will increase the import potential in period of low wind and solar generation. Also the system adequacy in southern Sweden is enhanced since it given more import capacity in a future with less available nuclear generation capacity. Increase of RES in both countries leads to higher need for trade with high surplus during high wind power production. Flows are to be balanced with southbound flow during peak hours and when hydro inflow in Sweden are high and northbound in periods of high German RES generation by night | 700 | 700
179 | DKE - DE (Kontek2) | This project includes a HVDC subsea interconnector between Denmark-East (DKE) and Germany (DE) and is called Kontek-2. A final grid-connection solution is not prepared yet. | DE ;DK | 2030 | 1 | True | False | FALSE |  | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to address system adequacy deficiencies and/or mitigate the risk of power failures. Infrastructure to tackle a Need identified by one of the European ITEG indicators referring to the 15% interconnection target for 2030: 1. Reduce the price differential between EU countries to below 2EUR/MWh. 2. Contribute to pushing ratio between nominal transmission capacity and installed RES capacity past 30%. 3. Contribute to pushing ratio between nominal transmission capacity and peak load past 30%. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | The project will serve as connection between the Nordic and central European power systems either transporting hydro power from the Nordic area to continental Europe or transporting wind and thermal power from the continent to the Nordics in times of low hydro levels. The project contributes new interconnection capacity to mitigate challenges in the DKE system. The project will enable the reduction of market price differential to below 2 EUR/MWh. The project will enable the integration of RES. More interconnection capacity will improve capability of balancing the system. | 600 | 600
183 | DKW-DE, Westcoast | New 400 kV line from Endrup (DK) to Klixbüll (DE), increasing the transfer capacity at the West Coast between these countries. The project is labelled by the EC as project of common interest (PCI 1.3.1). | DE ;DK | 2023 | 3 | True | False | TRUE | 1.3.1 | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to address system adequacy deficiencies and/or mitigate the risk of power failures. Infrastructure to improve system flexibility and stability e.g. improve system or local ramp rate, improve transient stability or RoCoF to meet system Needs. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | contributes to reduction of price spread by 2040 facilitates exchange of RES and reserves increases system size, thus facilitates sharing of ancillary service high RES increase expected on both sides of the border - further connection via P167 connecting to low correlated RES area | 1000 | 1000
186 | East of Austria | To allow the grid integration of the planned renewable energy generation (mainly wind power) in the north-eastern part of Austria ("Weinviertel") the transmission grid infrastructure (currently a rather weak 220kV line) has to be enforced and new substation for the connection needs to be erected. | AT | 2022 | 4 | False | True | FALSE |  | Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | Projects improves connection of wind generation with sufficient capacity to the transmission system and enables future RES development. Projects improves connection of wind generation with sufficient capacity to the transmission system and enables future RES development. | 2000 | 2000
187 | St. Peter (AT) - Pleinting (DE) | Increase of the cross border transmission capacity by erecting a new 380kV line between St. Peter (Austria) and Pleinting (Germany). This leads to an improved connection of the very high amount of RES in Germany and the pump storages in the Austrian Alps. | AT ;DE | 2028 | 3 | True | False | FALSE |  | Infrastructure to tackle a Need identified by one of the European ITEG indicators referring to the 15% interconnection target for 2030: 1. Reduce the price differential between EU countries to below 2EUR/MWh. 2. Contribute to pushing ratio between nominal transmission capacity and installed RES capacity past 30%. 3. Contribute to pushing ratio between nominal transmission capacity and peak load past 30%. Infrastructure to improve system flexibility and stability e.g. improve system or local ramp rate, improve transient stability or RoCoF to meet system Needs. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | helps to reach the target in Germany high RES generation connected to pump storage high RES generation connected to pump storage | 1500 | 1500
190 | NorthConnect | A 665 km long subsea interconnector between Norway and Scotland is planned to be realised in 2024. The interconnector is planned to be a 1400 MW HVDC subsea interconnector between western Norway (Simadalen) and eastern Scotland (Peterhead), UK. | GB ;NO | 2024 | 3 | True | False | TRUE | 1.10.2 | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to tackle a Need identified by one of the European ITEG indicators referring to the 15% interconnection target for 2030: 1. Reduce the price differential between EU countries to below 2EUR/MWh. 2. Contribute to pushing ratio between nominal transmission capacity and installed RES capacity past 30%. 3. Contribute to pushing ratio between nominal transmission capacity and peak load past 30%. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | NorthConnect reduce price spread between the hydropower dominated in bidding zone NO3 in and UK according to IoNS. The landing point Peterhead in Scotland has the highest share of RES in the UK and willl relieve internal congestion towards England (Price differentials are among the highest ) The UK ratio between nominal transmission capacity and installed RES is 14-18% in the TYNDP 2030 reference scenario (including NorthConnect), and the ratio between nominal transmission capacity and peak load is 20-21%. NorthConnect will contribute to improve the above mentioned ITEG indicators Curtailments in UK already exceeded 2.4 TWh (Sep 2020) and are expected to exceed 3 TWh by end of year. Norway also curtails hydropower in wet years. NorthConnect reduces RES curtailments both in UK and Norway. NorthConnect help utilise the complementaries of wind in UK and Norways 86.5 TWH of fhydropower reservoirs, which is about 50% of Europe's total storage capacity. NorthConnect will provide balancing power in periods of calm wind, and store energy in windy periods for RES in the UK | 1400 | 1400
197 | N-S Finland P1 stage 2 | This project is fifth 400 kV overhead line connecting North Finland to South Finland and required compensation investments. The project is to be built to increase the North-South transmission capacity thus enabling the integration of new renewable and conventional generation in northern Finland. | FI | 2022 | 4 | False | True | FALSE |  | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment Infrastructure to improve system flexibility and stability e.g. improve system or local ramp rate, improve transient stability or RoCoF to meet system Needs. |  | 1000 | 1000
200 | CZ Northwest-South corridor | A corridor of internal 400 kV overhead lines inside the Czech Republic connecting new 420 kV substations between Vernerov, Vitkov and existing substation Prestice in the northwest-south direction. The project consists building of two 400 kV overhead lines involving changing a 220 kV double-circuit lines to 400 kV double-circuit lines with a capacity of 2x1713 MVA each between Vernerov and Vitkov and Vitkov and Prestice. Part of the project is also a construction of a new 420 kV substation Vitkov and upgrading and extension of the existing 420 kV substation Kocin. | CZ | 2024 | 3 | False | True | TRUE | 3.11.1, 3.11.2, 3.11.4 | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. Contribution to the power system's operational flexibility by controlling power flows and optimizing use of existing infrastructure Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | This project helps to decrease the curtailed energy in Germany due to extra market transfers (increase of NTC) on the profile DE - CZ which lead to reduction of marginal price. This project besides the increase of NTC also consists of reinforcement of internal lines and therefore facilitates the future need for cross-border flows. The project contains the upgrade of existing 220 kV lines to 400 kV lines which will reduce infrastructure vulnerability and therefore ensure reliable and secure operation of the grid. The project is aiming at facilitation of the power flows from the RES generation in the northern part of Europe and western part of CZ therefore promotes RES integration. | 500 | 500
207 | Reinforcement Northwestern DE | Integration of on- and offshore RES in Lower Saxony | DE | 2023 | 4 | False | True | FALSE |  |  |  | 0 | 0
208 | N-S Western DE_section North_1 | Project 208 consists of a new 380 kV overhead line (partly in an existing corridor) for up to four 380 kV systems. The project is needed for integration of on- and offshore wind energy and transport to the load centres in western and southern parts of Germany. | DE | 2021 | 4 | False | True | FALSE |  |  |  | 0 | 0
210 | Wurmlach (AT) - Somplago (IT) interconnection | Somplago - Wurmlach interconnection is a cross-border electrical line promoted by Alpe Adria Energia Srl. The project concerns a 220kV a.c. merchant line, about 300 MW thermal capacity from Somplago substation to new Wurmlach substation, including Phase Shifter Transformer located in Austria. | AT ;IT | 2023 | 3 | True | False | TRUE | PCI 3.4 | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to address system adequacy deficiencies and/or mitigate the risk of power failures. Infrastructure to tackle a Need identified by one of the European ITEG indicators referring to the 15% interconnection target for 2030: 1. Reduce the price differential between EU countries to below 2EUR/MWh. 2. Contribute to pushing ratio between nominal transmission capacity and installed RES capacity past 30%. 3. Contribute to pushing ratio between nominal transmission capacity and peak load past 30%. Infrastructure designed to offer more supply options to isolated areas | The Project will enhance the interconnection capacity between the interconnected Countries and will allow a progressive alignment of the Italian border price differentials also in line with the interconnection target recommendations (Nov 2017) by EC Expert Group. The project will enhance the adequacy of the interconnected systems in the mid/long-term scenarios. In particular, it improves the share of the renewable energy sources and new flexible thermal generation in the electricity systems. The Project contributes to increase the Italian cross-border capacity in the medium-long term objectives (2030) as also reported in the Italian Implementation Plan for the requirements set in article 20 of Regulation 2019/943 of 5th June 2019 on the Internal Electricity Market (IEM). Considering that the Italian Peninsula is one of the most European isolated area, the Project will increase the Italian cross-transfer capacity contributing to reduce the gap with the other European Countries. | 150 | 150
219 | EuroAsia Interconnector | The Euro Asia Interconnector consists of a 500 kV DC underwater electric cable and any essential equipment and/or installation for interconnecting the Cypriot, Israeli and the Greek transmission networks (offshore). The Interconnector will have a capacity of 2000 MW and a total length of around 1200 km (approx. 310 km between CY and IL, 898 km between CY and Crete) and allow for reverse transmission of electricity. | CY ;GR ;IL | 2022 | 3 | True | False | TRUE | 3.10 |  |  | 1000 1000 | 1000 1000
225 | 2nd interconnector Belgium - Germany | This project considers the possibility of a second ~1GW HVDC interconnection between Belgium and Germany at the earliest by 2035 (indicative timing). The timing as well as location, routing, capacity are subject to further studies. Project motivation: Preliminary studies have indicated potential for further regional welfare increase by further increasing the interconnection capacity between Belgium and Germany. The possibility of higher market exchanges between these two bidding zones leads to a higher price convergence in more hours of the year and reduces therefore the price differentials. This interconnector project is designed as a HVDC-link. The full controllability of the HVDC link facilitates the balancing of active and reactive power in the Belgian and German grid. Belgium and Germany face decreasing figures of installed conventionals due to bad market conditions. The interconnector contributes to meet adecacy not only in both countries but also in the entire CWE-region. Due to the future RES increase in whole CWE the RES spillage will rise significantly especially beyond 2030. This interconnector project allows a better integration of RES in the entire region. | BE ;DE | 2035 | 1 | True | False | FALSE |  | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to address system adequacy deficiencies and/or mitigate the risk of power failures. Infrastructure to improve system flexibility and stability e.g. improve system or local ramp rate, improve transient stability or RoCoF to meet system Needs. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | This project increases the degree of interconnectivity between the Belgian and German bidding zones. The possibility of higher market exchanges between these two bidding zones leads to a higher price convergence in more hours of the year and reduces therefore the price differentials. Belgium and Germany face decreasing figures of installed conventionals due to bad market conditions. The interconnector contributes to meet adequacy not only in both countries but also in the entire CWE-region. This interconnector project between Belgium and Germany is designed as a HVDC-link. The full controllability of the HVDC link facilitates the balancing of active and reactive power in the Belgian and German grid. Due to the future RES increase in whole CWE the RES spillage will rise significantly especially beyond 2030. This interconnector project allows a better integration of RES in the entire region. | 1000 | 1000
227 | Transbalkan Corridor | This project contains seven investments, with the new corridor spanning from Central (SS Kragujevac 2 and SS Kraljevo 3) and Western Serbia (SS Obrenovac and SS Bajina Basta) all the way to SS Visegrad in Bosnia and Herzegovina and SS Lastva (across SS Pljevlja 2) in Montenegro. As can be seen from the brief list of the investments, the project aims to increase both the transmission capacity within Serbian transmission system and the transfer capacities on the borders between the mentioned countries. Thus, it is expected that it will largely facilitate the energy exchange between the north-east and south-west parts of Europe, setting a foundation for the enhanced market integration and leveling of the marginal energy costs and guaranteeing the security of supply throughout the region. This project is tightly connected to the projects 28 (Italy - Montenegro) and 342 (Central Balkan Corridor). | BA ;IT ;ME ;RS | 2026 | 3 | True | False | FALSE |  | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to address system adequacy deficiencies and/or mitigate the risk of power failures. Infrastructure to improve system flexibility and stability e.g. improve system or local ramp rate, improve transient stability or RoCoF to meet system Needs. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | As the Tranbalkan Corridor encompasses the infrastructure needed for the energy transfer across the Balkan Peninsula and towards Italy, it is envisaged as an invaluable tool for the market integration and consequential reduction of price differentials between Italy and the countries in Continental Southeast Europe region. As the grid in Western Serbia is rather old, which might put its reliability in question, one of the aspects that will also be affected by this project's commissioning is the increase of security of supply by replacing the numerous old power lines with the new ones. As the systems in this region are envisaged to heavily rely on the variable renewable sources in the not-so-distant future, the importance of new interconnections, such as those included in this project, for providing the additional system flexibility cannot be overstated. Even though the importance of this project for the RES integration might not be obvious, Drina river, located near the route of the lines enveloped by the project, offers huge potential for the future environmentally friendly Hydro Power Plants, amplifying the significance of Transbalkan Corridor for this system need. | 20 850 | 500 700
228 | Muhlbach - Eichstetten | Reinforcement of the existing 400kV OHL. Deployment of a second 400kV circuit at existing double circuit OHL Muhlbach - Eichstetten, instead of the currently operated circuit Eichstetten - Vogelgrun (currently operated with 225kV). Some topological adjustments of the existing grid in the area might prove to be necessary. This also include a transformer in Sierentz substation to balance flows between 225kV and 400kV grid in the area. Motivation for the project : Germany and also the CCS-Region is characterised by a significant increase in RES generation. The grid has to be developed in order to support these new exchange possibilities, facilitating the access to the most economic energy mix, while minimising grid congestions. High flows in both directions West-East and North-South are expected. The project strengthens the European single market. This project increases the interconnector capacity between France and Germany and therefore also the security of supply. | DE ;FR | 2025 | 2 | True | False | FALSE |  | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to address system adequacy deficiencies and/or mitigate the risk of power failures. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment Reduction of the loop flows occurrence in the borders between CZ-DE, DE-PL, DE-NL, BE-LU, FR-DE | Although this is not the main driver for this project, increase the interconnectivity between the German and French bidding zone give the possibility of higher market exchanges between these two bidding zones leading to a higher price convergence in more hours of the year. France and Germany face decreasing figures of installed conventionals due to reduction or phaseout of nuclear and bad market conditions for other conventionals. The interconnector contributes to meet adequacy not only in both countries but also in the entire CWE region. Rising figures of RES capacities especially in Germany lead to increasing RES-curtailment in the coming decades. This interconnector project allows a higher export in hours of high RES infeed particularly in Western Germany. Flows on 380kV OHL could be adjusted with both PSTs installed in Muhlbach substation rather than current 220kV interconnector. | 300 | 300
229 | GerPol Power Bridge II | Project consist from following investments: indentation to the one circuit of 400 kV line Baczyna-Plewiska (new routes 400 kV: Baczyna-Zielona Góra, Zielona Góra-Plewiska), crossborder line 2x400 kV line Zielona Góra (PL)-Eisenhuettenstadt (DE), new station Zielona Góra (with Phase Shifting Transformers), new 2x400 kV line Zielona Góra - Polkowice. | DE ;PL | 2035 | 1 | True | True | FALSE |  | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment Infrastructure to address system adequacy deficiencies and/or mitigate the risk of power failures. | Finalization of the GerPol Power Bridge II project allows to increase cross-border capacity on the Polish-German border and thus allows to exchange more energy. This project contributes to a reduction of unscheduled flows DE-PL, PL-CZ and PL-SK by increasing the controllability of the power flow on the DE-PL border. This project enables the integration of additional RES in the area of western and north-western Poland as well as in the eastern part of Germany. Project contributes to mitigate the risk of adequacy deficiencies in Germany and Poland by connecting areas with different mix of generation. | 1500 | 1500
230 | GerPol Power Bridge I | The reinforcements in the Polish transmission network in western part of the country near Polish/German border. Construction new AC 2x400 kV lines Mikułowa - Świebodzice, Krajnik - Baczyna and Baczyna - Plewiska. | PL | 2024 | 3 | False | True | TRUE | 3.14 (including 3.14.2, 3.14.3, 3.14.4) | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. | Finalization GerPol Power Bridge I project allows to increasing cross-border capacity on Polish-German border and thus allows to exchange more energy. This project enables the integration of additional RES on the area of western and north-western Poland as well as eastern part of Germany This project contributes to accommodate future scenarios and cross-border flows. | 1500 | 500
231 | Beznau - Tiengen | This project comprises the upgrade of a 220 kV crossborder line to 380 kV between the substations of Tiengen (DE) and Beznau (CH). | CH ;DE | 2030 | 1 | True | False | FALSE |  | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to address system adequacy deficiencies and/or mitigate the risk of power failures. Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. | This project contributes to lowering the price differentials between Switzerland on the one hand and Germany and Austria on the other hand. This project contributes to the adequacy in view of the nuclear phase-out and the development of renewables and pump hydro storage devices. This project is located in a highly meshed part of the transmission grid and therefore helps accommodate such flows. | 100 | 600
233 | Connection of Aragon Pumping hydro | Potential necessary transmission development for the connection of 3rd party storage project (pumping hydro) that has received a PCI label in the 3rd list 2017. No details about the required network are known yet (P1011 and P1019 in this TYNDP; take into consideration that these projects compete with each other as they use the same hydro resources). | ES | 2027 | 1 | False | True | FALSE |  | Infrastructure to improve system flexibility and stability e.g. improve system or local ramp rate, improve transient stability or RoCoF to meet system Needs. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | This project consists of the transmission network required for the connection of new pumping power plants that would give more flexibility to the system as the new pumping units will do. This project consists of the transmission network required for the connection of new pumping power plants that would allow RES integration | 3300 | 3300
234 | DKE - PL-1 | The first HVDC connector between Denmark-East and Poland. | DK ;PL | 2033 | 1 | True | False | FALSE |  | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | Project connects two market areas (DKE and PL) with high price differentials between EU countries. The project will enable the integration of RES. More interconnector capacity improves capability of balacing the system. | 600 | 600
235 | HVDC SuedLink Brunsbüttel/Wilster to Großgartach/Grafenrheinfeld | 4 GW HVDC connection from Northern Germany (areas of Brunsbüttel/Wilster) to Bavaria / Baden-Württemberg (areas of Großgartach/Grafenrheinfeld). North Germany is characterised by a high amount of RES, the feed-in exceeds the local load and therefore there is a high demand for transfer to the load centres in southern parts of Germany. With the further installation of additional renewable energy, the relevance of this projects increases. | DE | 2026 | 3 | False | True | FALSE |  | Infrastructure to improve system flexibility and stability e.g. improve system or local ramp rate, improve transient stability or RoCoF to meet system Needs. Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | Reducing the redispatch leading to more flexibility and increasing the stability of the system. In critical grid situations, costly congestion management measures are taken to avoid overload of grid elements. The project will reduce the demand for re-dispatching, countertrading and curtailment of renewable energy producers by adding significant transmission capacity between the congested routes in the North-Western part of Germany integration of huge amounts of offshore and onshore wind. | 4000 | 4000
239 | Fenno-Skan 1 renewal | Replacement of the existing 400 kV HVDC cable interconnection between Finland and Sweden. Fennoskan 1 will be decomissioned at the same time with this project being commisioned. | FI ;SE | 2035 | 1 | True | False | FALSE |  | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to address system adequacy deficiencies and/or mitigate the risk of power failures. Infrastructure to tackle a Need identified by one of the European ITEG indicators referring to the 15% interconnection target for 2030: 1. Reduce the price differential between EU countries to below 2EUR/MWh. 2. Contribute to pushing ratio between nominal transmission capacity and installed RES capacity past 30%. 3. Contribute to pushing ratio between nominal transmission capacity and peak load past 30%. Infrastructure to improve system flexibility and stability e.g. improve system or local ramp rate, improve transient stability or RoCoF to meet system Needs. |  | 800 | 800
241 | Upgrading of existing 220 kV lines between HR and BA to 400 kV lines | Upgrading of existing 220 kV lines between SS Dakovo (HR) and SS Tuzla/Gradacac (BA) to 400 kV lines. The project 241, has been proposed assessed in the TYNDP 2016, based on the results of common planning studies performed in the CSE Region during preparation of Regional investment plan 2015. The project assumes upgrade of existing 220 kV lines between SS Dakovo (HR) and SS Tuzla (BH) and SS Gradacac (BH) to 400 kV, with additional internal new double 400 kV line connecting SS Dakovo to existing 400 kV line Žerjavinec - Ernestinovo. This project is under consideration and there is a need for pre-feasibility study. | BA ;HR | 2032 | 1 | True | False | FALSE |  |  |  | 500 | 500
243 | New 400 kV interconnection line between Serbia and Croatia | Construction of new 400 kV interconnection line Sombor (RS) - Ernestinovo (HR), expected to provide a significant asset in terms of increasing the NTC between Serbia and Croatia, hence allowing the more prominent energy flow in the East-West direction across the CSE region, improving the market integration among the beneficiary countries and further ensuring the security of supply primarily in Serbia and Croatia, but, under certain circumstances, contributing to the reliable functioning of the systems in the rest of the countries in the region as well. Alongside that, it should be mentioned that the project will have a rather positive impact related to the possibility of integration of renewable energy sources in the Backa region. | HR ;RS | 2035 | 1 | True | False | FALSE |  | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. Infrastructure and/or market design to provide balancing flexibility (e.g. international pooling / sharing of reserves, coordinated development of reserve capacity) Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | Since this interconnection means the increase of NTC between Croatia (EU country) and Serbia (non-EU country), it is seen as a mean of reaching the market integration goals and reducing the price differentials in the Continental Southeast Europe region. As the future scenarios, taken into account in the scope of TYNDP, predict rather high energy flow across the borders in the CSE region, each of the new interconnections in that area can be seen as an additional step towards guaranteeing the timely reaching of the set goal. In the conditions of ever higher needs for the intensive cooperation between the neighboring TSOs, every new interconnection, such as the one included in this project, can be seen as the asset regarding the improvement of systems' flexibility and reliability of operation. According to the currently available information, the Bačka region in Northern Serbia is predicted to host several wind power plants of sustainable installed capacity, with the line between SS Sombor 3 and SS Ernestinovo ensuring the uninterrupted and secure evacuation of the produced energy. | 600 | 600
244 | Vigy - Uchtelfangen area | An upgrade of the existing over headline between the substations Ensdorf, Uchtelfangen and Vigy is planned to increase the thermal cross-border capacity. For this reinforcement the options are either the implementation of High Temperature Low Sag (HTLS) conductors or a reconstruction of the tie-line in the existing route. To allow an optimal use of the capacity increase the installation of phase shifter transformers (PSTs) is necessary. For these measures the substations have to be adjusted accordingly. Motivation for the project : Germany and also the CCS-Region is characterised by a significant increase in RES generation. The grid has to be developed in order to support these new exchange possibilities, facilitating the access to the most economic energy mix, while minimising grid congestions. High flows in both directions West-East and North-South are expected. The project strengthens the European single market. This project increases the interconnector capacity between France and Germany and therefore also the security of supply. | DE ;FR | 2028 | 2 | True | False | FALSE |  | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to address system adequacy deficiencies and/or mitigate the risk of power failures. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment Reduction of the loop flows occurrence in the borders between CZ-DE, DE-PL, DE-NL, BE-LU, FR-DE | Although this is not the main driver for this project, increasing the interconnectivity between the German and French bidding zone gives the possibility of higher market exchanges between these two bidding zones leading to a higher price convergence in more hours of the year. France and Germany face decreasing figures of installed conventionals due to reduction or phaseout of nuclear and bad market conditions for other conventionals. The interconnector contributes to meet adequacy not only in both countries but also in the entire CWE region. Rising figures of RES capacities especially in Germany lead to increasing RES-curtailment in the coming decades. This interconnector project allows a higher export in hours of high RES infeed particularly in Western Germany. RES infeed in the north of Germany often bypasses via Netherlands, Belgium and France. The project allows a better limitation of these loop flows via new PSTs on the French-German border. | 1500 | 1500
245 | Upgrade Meeden - Diele | Increase of the interconnection capacity between The Netherlands and Germany by adding one new phase shifting transformer and apply dynamic line rating on the existing 380 kV double circuit tie line between Meeden and Diele. | DE ;NL | 2021 | 4 | True | False | FALSE |  | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. Contribution to the power system's operational flexibility by controlling power flows and optimizing use of existing infrastructure Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | This project helps increase the cross-border capacity between Netherlands and Belgium. This will help reduce the price differentials between these different bidding zones This project increases phase shifting transformer capabilities helping reduce loop flows and distributing cross-border flows better Project increases phase shifting transformer capabilities which increases controlability of the power flows and optimizes further use of existing grid infrastructure Optimized use of existing internal and cross-border infrastructure to better accommodate high volumes of RES and reduce RES curtailment | 300 | 300
247 | AQUIND Interconnector | AQUIND Interconnector is a proposed High Voltage Direct Current (HVDC) subsea and underground electric power transmission link between Great Britain (Lovedean substation, Hampshire) and France (Barnabos switching station, Seine-Maritime) with a net transmission capacity of 2,000 MW. The interconnector is designed as two parallel monopole 1000 MW circuits employing Voltage Source Converter technology. The project will be able to: • Boost competition by providing access to wider electricity markets; • Help improve security of supply by creating additional source of supply and by providing ancillary services to the respective national grids; and • Increase sustainability of energy supply by helping to integrate more renewable energy sources. The project will consist of the following elements: • One converter station on each end of the link, • The 320 kV DC subsea cable route will be approximately 182 km in length between Eastney (UK) and Pourville (France). • The British 320 kV DC terrestrial cable route will be approximately 20 km long. • The French 320 kV DC terrestrial cable route will be approximately 36 km long. • The 400 kV AC cable routes are several hundred meters in France and UK. | FR ;GB | 2023 | 3 | True | False | FALSE |  | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment Infrastructure and/or market design to provide balancing flexibility (e.g. international pooling / sharing of reserves, coordinated development of reserve capacity) Infrastructure to tackle a Need identified by one of the European ITEG indicators referring to the 15% interconnection target for 2030: 1. Reduce the price differential between EU countries to below 2EUR/MWh. 2. Contribute to pushing ratio between nominal transmission capacity and installed RES capacity past 30%. 3. Contribute to pushing ratio between nominal transmission capacity and peak load past 30%. | Structural differences in the wholesale electricity prices between the electricity markets in GB and France clearly demonstrate the need for more capacity. By providing additional 2GW of interconnection capacity AQUIND Interconnector will reduce price differentials on a congested France - GB border. AQUIND will provide an opportunity for the efficient dispatch of renewables in GB, France and across connected markets. The additional cross-border capacity provided by AQUIND offers the opportunity to export additional power, that otherwise could be curtailed, during periods of high renewable generation. AQUIND Interconnector will facilitate more efficient generation dispatch in the connected markets required for cross-border balancing services By providing additional 2GW of interconnection capacity AQUIND will contribute to reaching the objectives of the European ITEG indicators in France and GB. | 2075 | 2075
250 | Merchant line Castasegna (CH) - Mese (IT) | The planned Transmission project is a merchant line on the swiss-italian border between Castasegna (CH) and Mese (IT). The planned Cable connection in 220 kV AC has a length of around 14 km, 13.5 of witch in Italy. In connection with the realisation of the project a Rationalisation of the 380 and 132 kV Grid in the region Mese (Provincia di Sondrio) is planned. The expected NTC increase is around 200-250 MW. | CH ;IT | 2024 | 3 | True | False | FALSE |  |  |  | 200 | 200
252 | Internal Belgian Backbone Center-East: HTLS upgrade Massenhoven-VanEyck-Gramme-Courcelles-Bruegel-Mercator | This project structurally strenghtens the central & eastern part of the internal Belgian backbone. The current conductors on the 380kV ring Massenhoven-VanEyck-Gramme-Courcelles-Bruegel-Mercator-Massenhoven will be replaced by HTLS conductors. The implementation starts with the upgrade of the Massenhoven-VanEyck section by 2024 as this is the weakest link only having 1 conductor at the moment. It then follows a phased approach running up to 2035. Phasing is subject to optimalisation in function of outage constraints (operational secutiry) and the evolution of the production park. Project motivation: This upgrade will be key to sustain price convergence whilst the power flows become increasingly more volatile and international. Where in the past the location of generation and load centers was quite stable over time, this will be much less the case with the future energy mix characterized by RES geographically spread out over Europe. Depending on the climatic conditions, flows can come from the north, east, south or west, and even change several times per day as wind fronts and clouds move from one hour to the next. Upgrading the existing internal corridors also ensures the potential to integrate new large power plants domestically. RES integration implies higher flows in the meshed AC-grid and thus increases the need for internal transmission capacity. This project satisfies this need in a cost-efficient manner.This project contributes to adequacy, as both new grid hosting capacity is created & as it supports other projects intending to increase cross border transmission capacity, and in particular for Belgium considering the nuclear phaseout. | BE | 2035 | 1 | False | True | FALSE |  | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to address system adequacy deficiencies and/or mitigate the risk of power failures. Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | The upgrade of the backbone ring will unlock the full potential of future cross border capacity investments allowing higher market exchanges between bidding zones and leading to a higher price convergence in more hours of the year. This project contributes to adequacy, as both new grid hosting capacity is created and as it supports other projects intending to increase cross border transmission capacity, and in particular for Belgium considering the nuclear phase out. This project contributes to resolving internal congestions, considering expected increased market exchanges which induce higher flows. RES integration implies higher flows in the meshed AC-grid and thus increases the need for internal transmission capacity. This project satisfies this need in a cost-efficient manner. | 1500 | 1500
253 | Upstream reinforcement in France to increase FR-CH capacity | The project consists in attracting the flows to the interconnection south of Lake Geneva in order to alleviate the congestion on the link west to Lake Geneva. This project is coupled with Project 333 "PST Foretaille" and will be implemented right after the implementation of PST in Foretaille. | CH ;FR | 2031 | 1 | True | False | FALSE |  | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to address system adequacy deficiencies and/or mitigate the risk of power failures. Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. Contribution to the power system's operational flexibility by controlling power flows and optimizing use of existing infrastructure | Figures 2.12 and 2.13 of IoSN report: average marginal price difference higher than 10€/MWh between France and Switzerland in future scenarios. Project has positive impact on SoS indicator. Project upgrades the thermal capacity requested for meeting the export increases that have an impact on French internal lines, such as Creys - St Vulbas. Phase-shifting transformer allows optimization of flows on the border. | 500 | 500
254 | HVDC Ultranet Osterath to Philippsburg | The Ultranet project consists of a 2 GW HVDC-connection from the Region of Osterath (Rhineland) to the Region of Philippsburg (Baden-Württemberg). It's a pilot project with DC circuits on the same pylons as AC lines and will therefore deliver profund knowledge.It represents a separate subsection for the large-scale transmission link from the North Sea coast to Baden-Württemberg (with P132). | DE | 2024 | 3 | False | True | TRUE | 2.9 | Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. Reduction of the loop flows occurrence in the borders between CZ-DE, DE-PL, DE-NL, BE-LU, FR-DE Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment Infrastructure to improve system flexibility and stability e.g. improve system or local ramp rate, improve transient stability or RoCoF to meet system Needs. | In connection with P132, the planned HVDC connection transports the energy of regenerative Energy sources in northern Germany directly to the demand regions of southern Germany. It strengthens the common German market area through targeted energy transport. The project reduces loop flows to Germany's neighboring countries by reducing bottlenecks in northern Germany and providing a transport task from western Germany to southern Germany The project enables the integration of offshore wind and onshore wind energy in combination with P132 and prevents potential bottlenecks in northern Germany and southern Germany. The project contributes significantly to security of supply and grid stability through the widespread integration of renewable energies in northern (wind offshore and onshore) and southern Germany (wind onshore). In particular, the system flexibility is increased by the use of HVDC converter. | 2000 | 2000
258 | Westcoast line | New 380-kV-line Heide/West – Klixbüll inside Schleswig – Holstein. Main focus of the project is the integration of onshore RES – mainly wind – in Western Schleswig-Holstein. The project is labeled as PCI 1.3.2. It is the southbound connection of PCI 1.3.1. and is necessary to increase the GTC between Denmark/West and Germany by 500 MW. | DE | 2022 | 4 | False | True | FALSE |  |  |  | 500 | 500
259 | HU-RO | 400 kV interconnection line between Hungary and Romania. In Romania, the following internal investments are necessary associated to this project: -new 400/220 kV transformer in substation Rosiori -reconductoring 220 kV OH line Urechesti-Tg. Jiu-Paroseni- Baru Mare-Hasdat -new 400/220 kV transformer in substation Resita | HU ;RO | 2030 | 1 | True | False | FALSE |  | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure and/or market design to provide balancing flexibility (e.g. international pooling / sharing of reserves, coordinated development of reserve capacity) | The project contributes to the increase of the transfer capacity across the border between Hungary and Romania. Increased cross-border capacities allow countries to exchange more energy and this will have an impact on reducing the marginal costs. The project creates an additional energy corridor between Hungary and Romania, and it can be claimed that it will provide balancing flexibility area for both sides. | 1117 | 685
260 | Project 260 – Multi-purpose HVDC interconnection between Great Britain and The Netherlands | This project considers a multi-purpose HVDC interconnection between Great Britain and The Netherlands, that combines the benefits of connecting electricity markets and offshore wind generation in Great Britain and The Netherlands. The base capacity of the cross border interconnection is around 2GW, but more can be considered. | GB ;NL | 2030 | 1 | True | False | TRUE | 1.16 |  |  | 2000 | 2000
262 | Belgium-Netherlands: Zandvliet-Rilland | Bilateral study has assessed multiple reinforcement options. The study concluded that an upgrade of the existing corridor Zandvliet-Rilland via the installation of two additional PSTs in Zandvliet and the upgrade of Zandvliet-Rilland line to high capacity conductors is the most appropriate solution. The constuction of the substation Rilland is part of TenneT's project ""Zuid-West 380"", id 346. Project motivation: A need has been identified during TYNDP16 and TYNDP18 to develop additional interconnection capacity between Belgium and The Netherlands. This project effectively increases the degree of interconnectivity between the Belgian and Dutch bidding zone. The possibility of higher market exchanges between these two bidding zones leads to a higher price convergence in more hours of the year and reduces therefore the price differentials. This project has an important adequacy contribution due to decreasing figures of installed conventionals (bad market conditions) and especially in light of the nuclear phaseout. RES integration implies higher flows in the meshed AC-grid and thus increases the need for cross border transmission capacity. This project satisfies this need in a cost-efficient manner. PSTs will also help to balance the flows over the different cross border lines of the Belgian Dutch interconnection.Based on the above, the project directly contributes to the interconnection criteria 2030. | BE ;NL | 2022 | 4 | True | False | FALSE |  | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to address system adequacy deficiencies and/or mitigate the risk of power failures. Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | This project increases the degree of interconnectivity between the Belgian and Dutch bidding zone. The possibility of higher market exchanges between these two bidding zones leads to a higher price convergence in more hours of the year and reduces therefore the price differentials. This project has an important adequacy contribution due to decreasing figures of installed conventionals and considering the nuclear phaseout in Belgium. The installation of phase shifting transformers will help to balance the flows over the different cross border lines on the Belgian-Dutch border. RES integration implies higher flows in the meshed AC-grid and thus increases the need for cross border transmission capacity. This project satisfies this need in a cost-efficient manner. | 1000 | 1000
263 | Lake Constance East | This project increases the capacity between CH and its neighbours DE and AT. This enables to connect large renewable generation in Northern Europe to consumers and pump storage devices in the Alps, thus noticeably increasing the mutual balancing between both regions. | AT ;CH ;DE | 2035 | 1 | True | False | FALSE |  | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to address system adequacy deficiencies and/or mitigate the risk of power failures. Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. | This project contributes to lowering the price differentials between Switzerland on the one hand and Germany and Austria on the other hand. This project contributes to the adequacy in view of the nuclear phase-out and the development of renewables and pump hydro storage devices. This project is located in a highly meshed part of the transmission grid and therefore helps accommodate such flows. | 100 600 1000 | 200 250 1000
264 | Swiss Roof I | This project increases the capacity between CH and its neighbours DE, AT and IT. This enables to connect large renewable generation in Northern Europe to pump storage devices in the Alps, thus noticeably increasing the mutual balancing between both regions. | CH | 2035 | 3 | False | True | FALSE |  | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to address system adequacy deficiencies and/or mitigate the risk of power failures. Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. | This project contributes to lowering the price differentials between Switzerland on the one hand and Germany and Austria on the other hand. This project contributes to the adequacy in view of the nuclear phase-out and the development of renewables and pump hydro storage devices. This project is located in a highly meshed part of the transmission grid and therefore helps accommodate such flows. | 400 1500 200 | 400 1500 0
265 | Tessin | Reinforcement of the infrastructure in canton Tessin. | CH | 2035 | 2 | False | True | FALSE |  | Infrastructure to address system adequacy deficiencies and/or mitigate the risk of power failures. Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. | This project contributes to the adequacy in view of the nuclear phase-out and the development of renewables and pump hydro storage devices. This project is located in a highly meshed part of the transmission grid and therefore helps accommodate such flows. | 200 | 200
266 | Swiss Ellipse I | The project helps accommodate new pump storage units which mainly support the increasing RES generation in the European areas with solar and wind generation and increase the DE-CH NTC. | CH | 2029 | 3 | False | True | FALSE |  | Infrastructure to address system adequacy deficiencies and/or mitigate the risk of power failures. Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. Infrastructure to reduce price differentials between EU and/or non-EU countries | This project contributes to the adequacy in view of the nuclear phase-out and the development of renewables and pump hydro storage devices. This project is located in a highly meshed part of the transmission grid and therefore helps accommodate such flows. This project contributes to lowering the price differentials between Switzerland on the one hand and Germany on the other hand. | 800 | 800
267 | Hansa PowerBridge II | Possible second HVDC cable interconnector between southern Sweden (Bidding area SE4) and Germany (50Hertz). This project candidate is driven by market based target capacities found in the Common Planning Studies by Regional Group Baltic Sea. | DE ;SE | 2035 | 1 | True | False | FALSE |  | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to address system adequacy deficiencies and/or mitigate the risk of power failures. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | The main driver is market integration of the Nordic hydro/nuclear/RES dominated system with the German thermal/RES based system. The infrastructure will reduce price differentials between EU countries. The system adequacy is enhanced in Germany which will increase the import potential in period of low wind and solar generation. Also the system adequacy in southern Sweden is enhanced since it given more import capacity in a future with less available nuclear generation capacity. Increase of RES in both countries leads to higher need for trade with high surplus during high wind power production. Flows are to be balanced with southbound flow during peak hours and when hydro inflow in Sweden are high and northbound in periods of high German RES generation by night | 700 | 700
270 | FR-ES project -Aragón-Atlantic Pyrenees | This project consist of a new HVDC interconnection between France and Spain located in the Central part of the Pyrenees between Aragón region (Spain) and Marsillon (France). Internal AC reinforcements in Spain complement the cross border section, in order to connect the new converter station to the existing network. This project was included in the 2015 and 2017 PCI list (PCI 2.27.1) | ES ;FR | 2030 | 2 | True | False | TRUE | 2.27.1 | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to tackle a Need identified by one of the European ITEG indicators referring to the 15% interconnection target for 2030: 1. Reduce the price differential between EU countries to below 2EUR/MWh. 2. Contribute to pushing ratio between nominal transmission capacity and installed RES capacity past 30%. 3. Contribute to pushing ratio between nominal transmission capacity and peak load past 30%. Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | The IoSN report show high price differentials in FR-ES that would be reduced with a project in this border. IoSN report shows that for the 2040 time horizon there is need for developing projects in the French-Spanish border. By increasing interconnection capacity on ES-FR border, the project contributes to enhance flow distribution and RES integration, and to increase exchanges between France and the Iberian Peninsula. TYNDP shows a reduction of RES spillage considering the increase of interconnection capacity in ES-FR. | 1500 | 1500
276 | FR-ES project -Navarra-Landes | This Project consist of a new HVDC interconnection between France and Spain in the Western part of the Pyrenees between Pamplona area (Spain) and Cantegrit (France). The project is considered as an HVDC project of 2x1000 MW. Internal reinforcements complement the cross border section. This project was included in the 2015 and 2017 PCI list (PCI 2.27.2) | ES ;FR | 2029 | 2 | True | False | TRUE | 2.27.2 | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to tackle a Need identified by one of the European ITEG indicators referring to the 15% interconnection target for 2030: 1. Reduce the price differential between EU countries to below 2EUR/MWh. 2. Contribute to pushing ratio between nominal transmission capacity and installed RES capacity past 30%. 3. Contribute to pushing ratio between nominal transmission capacity and peak load past 30%. Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | The IoSN report show high price differentials in FR-ES that would be reduced with a project in this border. IoSN report shows that for the 2040 time horizon there is need for developing projects in the French-Spanish border. By increasing interconnection capacity on ES-FR border, the project contributes to enhance flow distribution and RES integration, and to increase exchanges between France and the Iberian Peninsula. TYNDP shows a reduction of RES spillage considering the increase of interconnection capacity in ES-FR. | 1500 | 1500
280 | FR-BE: study Lonny-Achene-Gramme | The project aims at sustaining further market integration within the long-term perspective of the energy transition and subsequent need to develop interconnection capacity on the French-Belgium border whilst alleviating Lonny-Achene-Gramme as bottleneck.The reinforcement strategy consists of maximizing the potential of the 400kV interconnector Lonny-Achene-Gramme through the use of cost-efficient technologies such as PSTs and HTLS as well as the possibility to rebuild Lonny-Achene-Gramme as a 2-circuit solution. The bilateral study will determine the appropriate implementation option and phasing of this implementation (for example: first install a PST, then upgrade the line capacity), taking into account 1) the optimization of flows between the 400kV interconnectors Avelin-Avelgem-Horta & Lonny-Achene-Gramme 2) that by 2025 Lonny-Achene-Gramme is a structural bottleneck due to the planned nuclear phase out in Belgium, and as such a first implementation step (for example PST) is needed 3) gain in efficiency in developing a structure with 2 circuits versus current structure with 1 circuit on Lonny-Achene-Gramme Project motivation: With this project RTE and Elia investigate the possibilities to further develop interconnection capacity on the FR-BE border, in line with the signals provided by the 2030 interconnection target criteria as well as the identification of needs upon 2040 scenario's, illustrating that higher power flows will emerge from future production mixes with more RES. This project fits within the strategy to develop cost efficient upgrades of the existing AC interconnectors in the CWE area. | BE ;FR | 2030 | 1 | True | False | FALSE |  | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to tackle a Need identified by one of the European ITEG indicators referring to the 15% interconnection target for 2030: 1. Reduce the price differential between EU countries to below 2EUR/MWh. 2. Contribute to pushing ratio between nominal transmission capacity and installed RES capacity past 30%. 3. Contribute to pushing ratio between nominal transmission capacity and peak load past 30%. Contribution to the power system's operational flexibility by controlling power flows and optimizing use of existing infrastructure Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | This project increases the degree of interconnectivity between Belgium and France. The possibility of higher market exchanges between these two bidding zones leads to a higher price convergence in more hours yearly and reduces therefore the price differentials. This is also included as key trigger of the 2030 interconnection criteria. Based on IOsN report, 15% IC-target requires higher cross border transmission capacity. This project contributes to satisfy this need, provided that the project benefits outweigh its costs. With the potential use of PSTs to better balance flows between the different crossborders lines, it will reduce bottlenecks and consequently increase the exchanges on the boundary itself and also in CWE area. RES integration implies higher flows in the meshed AC-grid and thus increases the need for cross border transmission capacity. This project satisfies this need in a cost-efficient manner. | 1000 | 1000
283 | TuNur | TuNur aims at connecting to the European electricity network a Concentrated Solar Power (CSP) plant with storage and an overall capacity in excess of 2000 MW to be located in Rejim Maatoug, Kebili, Tunisia. The connection point to ENTSO-E’s network is located in Montalto di Castro, North of Rome, Italy. The transmission project will consist in a +/- 500 kV DC overhead line in Tunisia spanning from the power plant to the shoring point, submarine cables from the Tunisian Northern coast to Montalto di Castro, VSC HVDC converter stations at both terminal points, and short 400 kV AC cables from the HVDC converter in Montalto to Terna’s 400 kV station. No sea electrode is foreseen. | IT ;TN | 2026 | 1 | True | False | FALSE |  | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to address system adequacy deficiencies and/or mitigate the risk of power failures. Infrastructure to improve system flexibility and stability e.g. improve system or local ramp rate, improve transient stability or RoCoF to meet system Needs. Infrastructure and/or market design to provide balancing flexibility (e.g. international pooling / sharing of reserves, coordinated development of reserve capacity) | The TuNur project will contribute to improving market integration and reducing price differentials between EU and non-EU countries by providing an additional 2000 MW of low cost and low carbon available capacity, through a new connection between a non-EU (Tunisia) and EU (Italy). TuNur will provide dispatchable low-carbon power, thereby mitigating the risk of power failure, and will contribute to system adequacy deficiencies by increasing transmission capacity. This power source will improve security of supply by reducing Loss of Load durations across EU networks, making a significant contribution to system stability The TuNur project will significantly contribute to system flexibility through direct access to a new source of renewable energy. TuNur will also contribute to system stability by improving transient stability and helping to meet RoCoF system needs. TuNur will provide flexible power with black-start capacity. TuNur consists in infrastructure that will contribute to balancing flexibility by providing the European network with a new source of low-carbon dispatchable power. Additionally, the TuNur project will deliver a 2000 MW power reserve through a new HVDC interconnection between Tunisia and Italy. | 2000 | 2000
284 | LEG1 | LEG1 is a submarine HVDC interconnection project, enabling bidirectional electricity exchange between South-East Europe and North Africa. The interconnector will link the area of Tobruk, in Libya, to Linoperamata in Crete. Landing spots have been discussed with the respective TSOs. GreenPower2020 has identified an ideal submarine corridor (305 km) reaching a maximum depth of 2700m, providing one of the shortest possible links between continental Europe and North Africa, as Crete will be connected to continental Greece with a 1,000 MW DC interconnector in 2023. LEG1 interconnector will have a power rating of 2,000 MW and a DC voltage of 525 kV. VSC was chosen for converter technology because it is more favorable for power trading and has other advantages such as blackstart capacity and voltage stability support. LEG1 will also connect Libya to Egypt (Salloum) through AC overhead line with related substations, benefiting from Libya and Egypt solar projects (initial 150 MW plant included), further contributing to the achievement of the EC’s Green Deal 2030 objectives. It will play an essential role in optimizing competitive production and consumption, taking advantage of the strong weekly and seasonal imbalances - Fridays vs Sundays / winters vs summers | EG ;GR ;LY | 2025 | 1 | True | False | FALSE |  |  |  | 2000 | 2000
285 | GridLink | 1.4 GW HVDC electricity interconnector between UK and France Voltage Source Converter (VSC) Grid connection point (substations name): Kingsnorth (UK) and Warande (France) Total cable length (substation to substation) 160km (112km in UK and 48km in France) Two cables (MI) laid in a single trench Nominal voltage: ±525 kV Thermal limit (Imax): 1330 A Mvar capability range at terminals: 460 MVAr Bus-bar to bus-bar losses profile over MW range: 2.3% (33 MW) full load; 0% (0 MW) at zero load Annual Availability: 98% availability, 2% planned outages, 0% forced outages. Maximum single failure according to the design: 1.4GW UK Transmission network reinforcement required: Uses spare bay with minimum works at Kingsnorth substation France transmission network reinforcement: Extension to Warande substation Main environmental impact: reduction of CO2 emissions by substituting electricity from fossil fuels by generation from RES and nuclear power. No material environmental impacts during construction and operation. | FR ;GB | 2024 | 3 | True | False | TRUE | 1.7.5 |  |  | 1400 | 1400
286 | Greenlink | An electricity interconnector between Ireland and Wales, Greenlink brings significant benefits on both sides of the Irish Sea for energy security and the integration of renewable low carbon energy sources. For Ireland, it provides a natural link to the EU and Nordic electricity markets via Wales, England and Scotland. Greenlink will employ proven HVDC technology and is similar to the successful East West Interconnector between North Wales and Ireland. The cable route will run from existing substations in Great Island, Co. Wexford and Pembrokeshire in Wales connecting EirGrid and National Grid power systems. It is unobtrusive, being underground subsea cables with a converter station located at each connection point. Both Ireland and the UK have stated their support for increased interconnection and its strategic benefits. | GB ;IE | 2023 | 3 | True | False | TRUE | 1.9.1 |  |  | 500 | 500
293 | Southern Aegean Interconnector | The project refers to the construction of a submarine DC transmission link to connect the licensed RES plants, located on 23 small uninhabited islands at the South Aegean sea, with mainland Greece and the islands of Crete, Kos and the Dodecanese. The main link will be an HVDC link connecting the island of Levitha to both the metropolitan area of Athens and the island of Crete; the 400kV substation at Lavrion area will be the connection point in the Athens area and the substation of Atherinolakkos will be the connection point in Crete (located in the South-East coast). The capacity of each link will be 600 to 800MW both directions using HVDC (High Voltage Direct Current) XLPE insulated technology and both links will consist of two parallel cables in order to increase the reliability of each link. 3 conversion stations using HVDC VSC technology are foreseen in Lavrio, Levitha & Crete (Atherinolakkos). All the installations on the islands (converter stations, substations etc) will be of closed type using GIS technology. The project will provide 19TWh/year of wind energy, increasing the transfer capacity between mainland Greece and Crete-Kos islands. | EG ;GR | 2025 | 1 | False | True | FALSE |  | Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment Infrastructure designed to offer more supply options to isolated areas Infrastructure to address system adequacy deficiencies and/or mitigate the risk of power failures. Infrastructure to improve system flexibility and stability e.g. improve system or local ramp rate, improve transient stability or RoCoF to meet system Needs. | Currently non-interconnected islands face significant RES curtailments, as the conventional units available in each island do not meet the flexibility requirements in view of adapting to the RES generation profile. Such curtailments will be significantly reduced when the project is implemented. More the project will facilitate the cost efficient grid connection of the under development Wind Turbine Plants (approx. 600 MW installed power) with mainland Greece. The supply of currently non interconnected autonomous islands will be enhanced with via the development of Southern Aegean Interconnector. The increased RES (Wind Turbine) capacity penetration provided with the development of Southern Aegean Interconnector shall lead to significant enhancement of System Adequacy (LOLE & LOEE decrease). | 582 | 582
296 | Britib | EU Priority Corridor: NSI West Electricity. Category: Electricity Highway. Acronym: Bretagne-Britain-Iberia (BritIb). Interconnection project between South-West England (United Kingdom), Cordemais (France) and Basque Country (Spain) in a multiterminal HVDC configuration of 525-600 kV with 3 inputs/outputs of 1800 MW each, and a mostly subsea route from Spain to Great Britain along the French coast of about 1330 km in total. The project’s development started in 2009 and is aligned with the EU Parliament priorities established in EU Regulation 347/2013 (Annex I): NSI West Electricity corridor (2) and e-Highways area (11). The Britib project was included in TYNDP 2014, 2016 and 2018. | ES ;FR ;GB | 2026 | 1 | True | False | FALSE |  |  |  | 1800 1800 1800 | 1800 1800 1800
297 | BRABO II + III | Realization of a new 380 kV corridor between Zandvliet and Mercator consisting of a double-circuit AC overhead line, including a new substation 380kV in Lillo. Project motivation: BRABO II and III sustain the development of interconnection capacity on the Belgian North Border towards a broader scenario framework, hereby securing the supply of electricity around the Antwerp harbour area in light of the increasing industrial demand (mainly applicable to BRABO II), as well as developing capacity for the potential integration of new production in the Antwerp area (mainly aplicable to BRABO III). This project contributes to resolving internal congestions, considering expected high international transit & loop flows. This project increases the degree of interconnectivity between the Belgian and Dutch bidding zone. The possibility of higher market exchanges between these two bidding zones leads to a higher price convergence in more hours of the year and reduces therefore the price differentials.This project allows to deal with the growth in industrial consumption from the Antwerp harbour and to increase the grid hosting capacity for connection of new production capacity, thereby contributing to the overall adequacy of the system, especially relevant considering the nuclear phase out in Belgium.RES integration implies higher flows in the meshed AC-grid and thus increases the need for cross border transmission capacity. This project satisfies this need in a cost-efficient manner. | BE | 2025 | 3 | False | True | TRUE | 2.23 | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to address system adequacy deficiencies and/or mitigate the risk of power failures. Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | This project increases the degree of interconnectivity between the Belgian and Dutch bidding zone. The possibility of higher market exchanges between these two bidding zones leads to a higher price convergence in more hours of the year and reduces therefore the price differentials. This project allows to deal with the growth in industrial consumption from the Antwerp harbour and to increase the grid hosting capacity for connection of new production capacity, thereby contributing to the overall adequacy of the system, especially relevant considering the nuclear phase out in Belgium. This project contributes to resolving internal congestions, considering expected increased market exchanges inducing higher flows. RES integration implies higher flows in the meshed AC-grid and thus increases the need for cross border transmission capacity. This project satisfies this need in a cost-efficient manner. | 1000 | 1000
299 | SACOI3 | New HVDC line between Italy mainland, Corsica and Sardinia replacing existing link SACOI2. Due to an update of the list of cross-border projects interconnecting Italy with other Member States within 2020, the 2020 interconnection ratio of Italy has been updated accordingly (from previous value of 9% computed by ENTSO-E in TYNDP 2018 to roughly 8%). As the Interconnection level of 10% will not be reached by 2020, Italy is requested to investigate options of further interconnections. | FR ;IT | 2024 | 3 | True | False | TRUE | 2.4 | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment Infrastructure to improve system flexibility and stability e.g. improve system or local ramp rate, improve transient stability or RoCoF to meet system Needs. Infrastructure to tackle a Need identified by one of the European ITEG indicators referring to the 15% interconnection target for 2030: 1. Reduce the price differential between EU countries to below 2EUR/MWh. 2. Contribute to pushing ratio between nominal transmission capacity and installed RES capacity past 30%. 3. Contribute to pushing ratio between nominal transmission capacity and peak load past 30%. | This project contributes to lowering the price differentials between Italian market zones and Corsica This project will improve the integration of italian RES generation This project will contribute to overcome flexibility/stability problems due to scarsely meshed grid This project helps Italy to reach the 15% interconnection target by 2030 | 400 | 400
309 | NeuConnect | NeuConnect will be the first subsea HVDC electricity Interconnector to connect the UK and German electricity markets. It will be approximately 700km long with a capacity of 1.4GW. This large capacity Interconnector has the advantage of accelerating the European wide ambition to create a single, competitive and efficiently driven electricity market for the benefit of consumers. | DE ;GB | 2022 | 3 | True | False | TRUE | 1.20 |  |  | 1400 | 1400
312 | St. Peter (AT) - Tauern (AT) | This project is part of the Austrian 380-kV security ring. It therefore provides based on the concept a redundant and robust connection and increases security of supply significantly. In addition higher transport capacities are able to connect RES production in the corners of the region with the Alpine storages and therefore integrate both efficiently and properly. | AT | 2035 | 4 | False | True | TRUE | 3.1.2 | Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment Infrastructure to tackle a Need identified by one of the European ITEG indicators referring to the 15% interconnection target for 2030: 1. Reduce the price differential between EU countries to below 2EUR/MWh. 2. Contribute to pushing ratio between nominal transmission capacity and installed RES capacity past 30%. 3. Contribute to pushing ratio between nominal transmission capacity and peak load past 30%. Infrastructure to improve system flexibility and stability e.g. improve system or local ramp rate, improve transient stability or RoCoF to meet system Needs. | Interconnection between huge amounts of RES and storage capacity in the Alps helps to reduce the amount of RES curtailment significantly facilitates interconnection capacity Interconnection between huge amounts of RES and storage capacity in the Alps provides flexibility and stability. | 2000 | 2000
313 | Isar/Altheim/Ottenhofen (DE) - St.Peter (AT) | New 380kV Line between TenneT-DE and APG (Isar/Altheim/Ottenhofen - St. Peter). This project reinforces the interconnection capacity between Austria and Germany. It supports the interaction of RES in Northern Europe (mainly in Germany) and in the eastern part of Austria with the pump storages in the Austrian Alps and therewith facilitates their utilisation. | AT ;DE | 2035 | 3 | True | False | TRUE | PCI 3.1.1 | Infrastructure to tackle a Need identified by one of the European ITEG indicators referring to the 15% interconnection target for 2030: 1. Reduce the price differential between EU countries to below 2EUR/MWh. 2. Contribute to pushing ratio between nominal transmission capacity and installed RES capacity past 30%. 3. Contribute to pushing ratio between nominal transmission capacity and peak load past 30%. Infrastructure to improve system flexibility and stability e.g. improve system or local ramp rate, improve transient stability or RoCoF to meet system Needs. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | helps to reach 15% target in Germany high RES generation connected to pump storage high RES generation connected to pump storage | 2000 | 2000
320 | Slovenia-Hungary/Croatia interconnection | The project consists of a new 80km double circuit 400kV OHL in Slovenia (section Cirkovce-Pince) and a new 400 kV substation of Cirkovce(SI). The new double 400 kV overhead line will be connected to one circuit of the existing double circuit 400kV OHL Heviz(HU)-Zerjavinec(HR). By this two new cross-border lines will be established - Heviz(HU)-Cirkovce(SI) and Cirkovce (SI)-Zerjavinec (HR). | HR ;HU ;SI | 2021 | 4 | True | False | TRUE | 3.9.1 | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to address system adequacy deficiencies and/or mitigate the risk of power failures. Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. Infrastructure and/or market design to provide balancing flexibility (e.g. international pooling / sharing of reserves, coordinated development of reserve capacity) | Project 320 will establish the first cross-border connection between Slovenia and Hungary, by which a new border and new transmission capacity with up to 1200 MW in both directions will be established. Project will increase market integration in the region, facilitate access to Eastern electricity markets and decrease price differentials in the region. Project 320 will increase system flexibility and stability, improve operational reliability and by this improve security of supply. This is expected also in cases of extraordinary grid events (blackouts, extreme weather events, outages of major generation units or other unforeseen events) where the Project will assure important new and reliable transmission capacity to overcome such problems. Furthermore, project is also essential for successful completion of smart grid project SINCRO.GRID, which will, jointly with project 320 regionally assure regional voltage regulation and regional voltage stability and thus system stability. In future scenarios production from RES sources will increase greatly, having also an influence on the power flows. Project will significantly increase transmission capacities and assure a higher level of security of supply, by which a positive effect on accomodation of power flows from new RES generation will be possible and in essence an increase of the amount of new RES integration. By realization of Project 320, also smart grid project SINCRO.GRID (PCI 10.3) will be completed, by which the level of regional system stability will be raised, having a direct effect on increased integration of additional RES generation in this region. With the project the first connection between Slovenia and Hungary will be established. By this reserve sharing will be possible, this demontrasted also in scope of project FutureFlow. | 1200 0 | 1200 150
322 | Wullenstetten - Border Area (DE-AT) | Between point Wullenstetten and point border area (DE-AT) as well as between Herbertingen and Point Neuravensburg, an upgrade of an existing 380-kV-line is necessary (grid enhancement). Furthermore, between switching point Neuravensburg and Austrian National border (AT) a new line with a significantly higher transmission capacity will be constructed in an existing corridor (grid enhancement). Thereby, a significantly higher transmission capacity is realized. | DE | 2025 | 2 | False | True | FALSE |  | Infrastructure to tackle a Need identified by one of the European ITEG indicators referring to the 15% interconnection target for 2030: 1. Reduce the price differential between EU countries to below 2EUR/MWh. 2. Contribute to pushing ratio between nominal transmission capacity and installed RES capacity past 30%. 3. Contribute to pushing ratio between nominal transmission capacity and peak load past 30%. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | The project increases the German interconnection level to Austria. The project helps connecting German RES power with pump storages in Austria and therefore improves the accomodation of flows. | 0 | 0
323 | Dekani (SI) - Zaule (IT) interconnection | The Zaule (IT) - Dekani (SI) interconnection is a third party cross-border electrical line promoted by Adria Link Srl, E3, ENERGETIKA, EKOLOGIJA, EKONOMIJA, d.o.o.. and Holding Slovenske Elektrarne d.o.o.. The project concerns an underground cable 110kV a.c. merchant line, 150 MW from Zaule (IT) substation to Dekani (SI) substation, including a 110/135 kV Phase Shifter Transformer. | IT ;SI | 2021 | 3 | True | False | FALSE |  | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to address system adequacy deficiencies and/or mitigate the risk of power failures. Infrastructure to tackle a Need identified by one of the European ITEG indicators referring to the 15% interconnection target for 2030: 1. Reduce the price differential between EU countries to below 2EUR/MWh. 2. Contribute to pushing ratio between nominal transmission capacity and installed RES capacity past 30%. 3. Contribute to pushing ratio between nominal transmission capacity and peak load past 30%. Infrastructure designed to offer more supply options to isolated areas | The Project will enhance the interconnection capacity between the interconnected Countries and will allow a progressive alignment of the Italian border price differentials also in line with the interconnection target recommendations (Nov 2017) by EC Expert Group. The project will enhance the adequacy of the interconnected systems in the mid/long-term scenarios. In particular, it improves the share of the renewable energy sources and new flexible thermal generation in the electricity systems. The Project contributes to increase the Italian cross-border capacity in the medium-long term objectives (2030) as also reported in the Italian Implementation Plan for the requirements set in article 20 of Regulation 2019/943 of 5th June 2019 on the Internal Electricity Market (IEM). Considering that the Italian Peninsula is one of the most European isolated area, the Project will increase the Italian cross-transfer capacity contributing to reduce the gap with the other European Countries. | 125 | 125
324 | Redipuglia (IT) - Vrtojba (SI) interconnection | "The Redipuglia (IT) - Vrtojba (SI) interconnection is a third party cross-border electrical line promoted by Adria Link Srl, E 3, ENERGETIKA, EKOLOGIJA, EKONOMIJA, d.o.o. and Holding slovenske elektrarne d.o.o.. The project concerns an underground cable 110kV a.c. merchant line, 150 MW from Redipuglia (IT) substation to Vrtojba (SI) substation, including a 110/135 kV Phase Shifter Trasformer." | IT ;SI | 2021 | 3 | True | False | FALSE |  | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to address system adequacy deficiencies and/or mitigate the risk of power failures. Infrastructure to tackle a Need identified by one of the European ITEG indicators referring to the 15% interconnection target for 2030: 1. Reduce the price differential between EU countries to below 2EUR/MWh. 2. Contribute to pushing ratio between nominal transmission capacity and installed RES capacity past 30%. 3. Contribute to pushing ratio between nominal transmission capacity and peak load past 30%. Infrastructure designed to offer more supply options to isolated areas | The Project will enhance the interconnection capacity between the interconnected Countries and will allow a progressive alignment of the Italian border price differentials also in line with the interconnection target recommendations (Nov 2017) by EC Expert Group. The project will enhance the adequacy of the interconnected systems in the mid/long-term scenarios. In particular, it improves the share of the renewable energy sources and new flexible thermal generation in the electricity systems. The Project contributes to increase the Italian cross-border capacity in the medium-long term objectives (2030) as also reported in the Italian Implementation Plan for the requirements set in article 20 of Regulation 2019/943 of 5th June 2019 on the Internal Electricity Market (IEM). Considering that the Italian Peninsula is one of the most European isolated area, the Project will increase the Italian cross-transfer capacity contributing to reduce the gap with the other European Countries. | 20 | 120
325 | Obersielach (AT) - Podlog (SI) | Obersielach (AT) - Podlog (SI); 380-kV Upgrade; +500 MW NTC in both directions | AT ;SI | 2034 | 1 | True | False | FALSE |  | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to address system adequacy deficiencies and/or mitigate the risk of power failures. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | Project increases capacity of SI-AT border and decreases price difference between both markets in all future scenarios. This project will contribute to redution of system adequacy deficiencies by increasing transmission capacity on SI-AT border. This project improves the integration of RES generation into the Continental European transmission grid. | 500 | 500
328 | Interconnector DE-LUX | The project comprises the construction of two new 380/220-kV-substations in Germany (Aach) and Luxemburg (Bofferdange). The new substations will be connected via a new AC-link to allow a higher cross border capacity between Germany and Luxembourg. | DE ;LU | 2026 | 2 | True | False | FALSE |  | Infrastructure to address system adequacy deficiencies and/or mitigate the risk of power failures. Infrastructure to improve system flexibility and stability e.g. improve system or local ramp rate, improve transient stability or RoCoF to meet system Needs. Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. |  | 1000 | 1000
329 | Stevin-Izegem/Avelgem (Ventilus): new corridor | The development of ~6 GW transport capacity through the elaboration of a new corridor in the western part of Belgium, between the Stevin axis and the Izegem/Avelgem substation. Should the corridor end in Izegem, it is to be complemented with an HTLS upgrade of the existing Izegem-Avelgem connection. Along this corridor a substation functioning as 'gateway' for the evacuation of offshore potential is envisioned. This corridor is envisioned to be implemented in AC technology following the example of the Stevin project. Timing, routing, scope, etc. subject to feasibility studies and subsequent spatial planning procedures. Project motivation: The capacity of the Stevin axis will be fully used by 2020 for the integration of the first wave of 2.3 GW offshore wind in the Belgian North Sea and Nemo Link. A further development of the 380 kV grid via a new corridor towards the coast creates the necessary perspective to unlock the energetic potential of the North Sea beyond 2020, including but not limited to the development of additional offshore wind in the Belgian part of the North sea. This new corridor will be linked to the Stevin corridor, creating a meshed 380 kV grid structure and considerably increasing the reliability. | BE | 2028 | 2 | False | True | FALSE |  | Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. Contribution to the power system's operational flexibility by controlling power flows and optimizing use of existing infrastructure Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | This project contributes to resolving internal congestions, considering expected high international flows as well as internal grid flows due to increased market exchanges. This projects foresees the installation of phase shifting transformers enabling power flow control and optimizing the use of existing infrastructure. This project creates the necessary onshore grid capacity to facilitate offshore wind development. This project will facilitate further offshore development and create grid hosting capacity for onshore and offshore RES development. | 6000 | 6000
330 | 4th 400kV CZ-SK interconnector | This new 400 kV cross-border overhead line between the substations Otrokovice (CZ) - Ladce (SK) will strenghten the transmission capacity between Slovak and Czech transmission systems, aiming to maintain secure operation of both transmission systems. | CZ ;SK | 2035 | 1 | True | False | FALSE |  | Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. Contribution to the power system's operational flexibility by controlling power flows and optimizing use of existing infrastructure Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | This project increases the NTC on CZ - SK profile and therefore facilitates the future need for cross-border flows and improves operational security. The project replaces the decommissioning of the two 220 kV interconnectors on the CZ - SK profile. In this way the secure operation of both transmission systems and the power exchange will be ensured. The project is aiming at facilitation of the power flows from the RES generation in the northern part of Europe and eastern part of CZ therefore promotes RES integration. | 500 | 500
333 | PST Foretaille | Installation of two PSTs in Foretaille that control the flow on the Foretaille - Verbois 220 kV double line | CH | 2031 | 1 | False | True | FALSE |  | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to address system adequacy deficiencies and/or mitigate the risk of power failures. Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. | This project contributes to lowering the Price differentials between France on the one hand and Switzerland on the other hand. This project contributes to the adequacy in view of the nuclear phase-out and the development of renewables and pump hydro storage devices. This project is located in a highly meshed part of the transmission grid and therefore helps accommodate such flows. | 100 | 1000
335 | Project 335 - North Sea Wind Power Hub | TenneT Netherlands, TenneT Germany, Energinet, Gasunie and Port of Rotterdam joined forces to develop a large scale European electricity system for offshore wind in the North Sea. The North Sea Wind Power Hub (NSWPH) consortium partners consider the project to be an im-portant possible alternative path of an internationally coordinated roll-out towards accom-plishing the green energy transition and achieving the Paris Agreement. Central to the vision is the construction of one or more hubs at a suitable location in the North Sea with interconnectors to bordering North Sea countries. The whole system may function as a hub for transport of wind energy, an interconnection hub to the connected countries, a working hub for offshore wind developers and a location for possible power-to-gas solutions. This project is a first building block in the hub-and-spoke concept (NSWPH) connecting up to 12 GW future offshore wind parks to the systems of Denmark, the Netherlands and Germany after 2035. Analysis by Roland Berger (commissioned by the EC) on this innovative project has shown that the hub-and-spoke concept provides significant cost savings (EUR 3.6bn over a 25year span) compared with the current, traditional, point-to-point interconnections and individual connec-tions for offshore windfarms (see Additional Information for source). An integral part of the NSWPH is to assess the perspectives of coupling large-scale wind power production with the gas system through power-to-gas (PtG) technology. The combination of cost-efficient infrastructure and the flexibility offered by the gas system may very well outweigh conversion losses, increasing the value of wind production and contribute to synergy effects through sector coupling in the transition of the energy system (see additional information). Several studies examining the benefits of PtG solutions can be found under “Additional Infor-mation”. As such the NSWPH infrastructure offers benefits by optimising integration costs of offshore wind, increasing socio-economic welfare by further coupling energy markets, supporting secu-rity of supply at wider regional level and providing potential to innovative power-to-gas con-cepts to optimise total energy system costs. | DE ;DK ;NL | 2035 | 1 | True | False | TRUE | 1.19 | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | The NSWPH entails deployment of new offshore wind capacity, which will be connected to European countries (NL, DK, DE). In addition, the new interconnection capacity via the hub will support the reduction of price differentials between EU countries. The infrastructure in relation to the NSWPH can accomodate future scenarios and cross-border flows, reducing the congestions in the onshore transmission system. The infrastructure in relation to the NSWPH, including combined grid connection and interconnection (and possibly large scale sector coupling) optimise large scale cost efficient integration of offshore wind. | - | -
336 | Prati (IT) – Steinach (AT) | New Italy-Austria tie-line between the existing 110kV Steinach substation in Austria and 132 kV Brennero substation, including PST; and connection to 132 kV Prati di Vizze substation. Due to an update of the list of cross-border projects interconnecting Italy with other Member States within 2020, the 2020 interconnection ratio of Italy has been updated accordingly (from previous value of 9% computed by ENTSO-E in TYNDP 2018 to roughly 8%). As the Interconnection level of 10% will not be reached by 2020, Italy is requested to investigate options of further interconnections. | AT ;IT | 2023 | 4 | True | False | FALSE |  | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to address system adequacy deficiencies and/or mitigate the risk of power failures. Infrastructure to tackle a Need identified by one of the European ITEG indicators referring to the 15% interconnection target for 2030: 1. Reduce the price differential between EU countries to below 2EUR/MWh. 2. Contribute to pushing ratio between nominal transmission capacity and installed RES capacity past 30%. 3. Contribute to pushing ratio between nominal transmission capacity and peak load past 30%. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | This project contributes to lowering the price differentials between Italian market zones and Austria. This project will contribute to reduce system adequacy deficiencies by increasing transmission capacity. This project helps Italy reach the 10% target by 2020 and 15% target by 2030. This project will improve the integration of Italian RES generation | 90 | 90
338 | Adriatic HVDC link | New HVDC line between Villanova (or Villavalle) and Fano (or Portotolle) existing 400 kV substations (the nominal power of the link will be at least 1000 MW) | IT | 2030 | 2 | False | True | FALSE |  | Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. Contribution to the power system's operational flexibility by controlling power flows and optimizing use of existing infrastructure | The new line will allow congestion reduction on the Southern-Northern border, and the integration of the local renewable production. Increasing of the Social Economic Welfare and reduction of the ancillary market services. | 600 1000 | 1000 1000
339 | Italian HVDC tri-terminal link | Italian HVDC link between Campania, Sicily and Sardinia | IT | 2025 | 2 | False | True | FALSE |  | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to improve system flexibility and stability e.g. improve system or local ramp rate, improve transient stability or RoCoF to meet system Needs. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | Increase market exchanges between market zones Increase of security of supply increase RES integration | 1000 1000 | 1000 1000
340 | Avelgem-Center: new corridor (Boucle du Hainaut) | The development of ~6 GW transport capacity through the elaboration of a new corridor between the Avelgem substation and the center of the Belgium (substation to be determined along the axis Bruegel-Courcelles). This corridor is envisioned to be implemented in AC technology as per the example of the Stevin project. Timing, routing, scope, etc. subject to feasibility studies and subsequent spatial planning procedures. Project motivation: Today, the west and the center of the country are connected on 380 kV via only one corridor between Mercator and Horta, which is currently being upgraded to HTLS. Additional capacity between the west and the center is, however, required to sustain price convergence within a European merit order increasingly characterized by RES. A new corridor between Avelgem and the center of the country would deliver around 6 GW of capacity and at the same time increases the maintainability and reliability of the grid, fulfilling the regulatory expectation that internal grids should be sufficiently strong so that society can fully reap the benefits from European market integration. Furthermore, the Avelgem – Center corridor is a pre-requisite for the integration of new offshore production capacity, for the connection of new large power plants west of Mercator, and for the integration of a second interconnector with Great-Britain (Nautilus). | BE | 2028 | 2 | False | True | FALSE |  | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. Contribution to the power system's operational flexibility by controlling power flows and optimizing use of existing infrastructure Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | This project deals with future more frequently expected situations with coinciding imports from France and UK together with evacuation of offshore wind. This project contributes to sustain price convergence between regions. Increased redundancy of onshore path ways will put less restrictions on cross border transmissions capacity for the market. This project contributes to resolving internal congestions, considering expected high international flows as well as internal grid flows due to increased market exchanges. This projects foresees the installation of phase shifting transformers enabling power flow control and optimizing the use of existing infrastructure. This project creates the necessary onshore grid capacity to facilitate offshore wind development. This project will facilitate further offshore development and create grid hosting capacity for onshore and offshore RES development. | 6000 | 6000
341 | North CSE Corridor | This project will consist of three investments. The investments of this project are SS 400/110 Belgrade West, OHL 400 kV SS Belgrade West - WPP Cibuk and doubling existing OHL 400 kV Portile de Fier (RO) - Djerdap 1 (RS). Every investment included in this project represents a segment of the new significant corridor in the East-to-West direction, boasting the massive cross-border impact on the boundary between Serbia and Romania. This, in detail, means that the project will enhance the market integration in the region, allowing the lower difference in marginal energy costs, allow the connection of huge capacities of renewable sources that have applied for connection in the observed area (only in Serbia, there is about 3 GW of new wind and solar power plants foreseen in the Banat region) and affect the security of supply in the aforementioned region by increasing the available balancing capacity across the mentioned border. It is clear that the new renewable capacities, enabled for connection by this project's commissioning, will enormously change the generation mix in Serbia and provide a boost for the Serbian transition towards the sustainable and environmentally acceptable green energy production. | RO ;RS | 2030 | 2 | True | False | FALSE |  | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to address system adequacy deficiencies and/or mitigate the risk of power failures. Infrastructure and/or market design to provide balancing flexibility (e.g. international pooling / sharing of reserves, coordinated development of reserve capacity) Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | As the project contributes to the increase of the transfer capacity across the border between Serbia and Romania, it is safe to claim that it will enhance the market integration in the region and reduce the price differentials, as requested by this need. The internal investments in Serbia, included in the scope of North CSE Corridor, are foreseen to mitigate the risks of potential blackouts in the Belgrade region. Investment SS Belgrade West will provide major help in reducing the loading of the existing 400/x and 220/x kV substations in Srem area. Due to the fact that the commissioning of this project creates an additional energy corridor between Serbia and Romania, as confirmed by the NTC calculations, it can be claimed that it will, among other benefits, prove to be a major asset in the balancing flexibility area for both sides. As the Banat region in the close proximity of the border between Serbia and Romania offers a great possibility for the connection of renewable sources, the investments enveloped by this project will most certainly help the safe and reliable placement of the produced energy in the systems of interest. | 347 | 622
342 | Central Balkan Corridor | This corridor will enable transmission of energy from east to west on the border between Bulgaria to Serbia and further to Montenegro and Bosnia and Herzegovina. It consists of several investments from SS Sofia West on the east to SS Pljevlja 2 and SS Visegrad on the west. In that way this corridor will be directly connected with project Transbalkan corridor (therefore, enabling the connection between Bulgarian energy market and Italian energy market), which represent a direct prerequisite for the proper development of the Central Balkan corridor. Among the numerous other benefits expected once this project is commissioned, the increase of NTCs on the borders between the involved countries (implying both the market integration and additional resources in securing the reliability of transmission systems' operation) can be seen as one of the most prominent. | BA ;BG ;ME ;RS | 2034 | 2 | True | False | FALSE |  | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to address system adequacy deficiencies and/or mitigate the risk of power failures. Infrastructure to improve system flexibility and stability e.g. improve system or local ramp rate, improve transient stability or RoCoF to meet system Needs. Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. | The Central Balkan corridor, among other investments, also includes strengthening of the interconnections in the CSE region (that involves both EU and non-EU countries), enhancing the market integration in the area of interest and, hence, succeeding in reducing the price differentials. As the project envelops the replacement of severely ageing 220 kV infrastructure in Central Serbia with the new 400 kV lines and substations, it is expected to significantly improve the system reliability in this area, thus reducing the possibility of putting the security of supply at risk in some operational regimes. Since the project of Central Balkan corridor offers the new interconnections between Serbia and several neighboring countries, it is most certainly envisaged as valuable improvement regarding the system flexibility, the full impact of which becoming apparent in the light of rapidly developing renewable energy sources in the CSE region. As the relevant scenarios, taken into account in the scope of the analyses carried out in the scope of TYNDP 2020, consider the significant flows across the borders in the CSE region, the NTC increases, caused by this project, might prove to be crucial for the involved systems. | 500 500 730 | 500 500 186
343 | CSE1 New | The project will contribute in strengthen Croatian transmission grid along its main north-south axis (in parallel with eastern Adriatic coast) allowing for additional long-distance power transfers (including cross border) from existing and new planned power plants (RES/wind/ and conventional/hydro and thermal/) in Croatia (coastal parts) and BiH to major consumption areas in Italy (through Slovenia) and north Croatia. The increased transfer capacity will support market integration (particularly between Croatia and Bosnia-Herzegovina) by improving security of supply (also for emergency situations), achieving higher diversity of supply & generation sources and routes, increasing resilience and flexibility of the transmission network. | BA ;HR | 2030 | 2 | True | False | FALSE |  |  |  | 644 | 298
344 | Reinforcements Ring NL phase II | Upgrade of existing 380kV circuits from 2,5 kA to 4 kA | NL | 2040 | 1 | False | True | FALSE |  | Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | Upgrade of the internal grid helps solve important congestions that arise due to future scenarios. Upgrade of the internal grid to help accommodate transport of high volumes of RES and thus decrease curtailment of RES | 0 | 0
346 | ZuidWest380 NL Oost | New 380 kV connection between Rilland and Tilburg including new substation. | BE ;NL | 2029 | 3 | False | True | FALSE |  | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | Upgrade of the internal grid helps increase the cross-border exchange capabilities Netherlands and Belgium reducing thus price differentials between these different bidding zones Due to the change of the generation mix in both countries as well as the need to increase the interconnection capacity between the two countries, a new pattern of power flows will be created. This project, in combination with projects 262 and 297, helps facilitate these new needs and flow patterns By upgrading existing parts of the transmission grid, but also creating new corridors in it, a cost-efficient integration of large amounts of offshore wind production is implemented and thus reduces possible RES curtailment. | 1000 | 10000
348 | NoordWest380 NL | Upgrade of existing 220kV circuits between Eemshaven and Vierverlaten to 2* 380kV – 2645MVA circuits | NL | 2023 | 4 | False | True | FALSE |  | Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | Due to the connection of new offshore wind power production in the north, as well as, the COBRA interconnector, a new pattern of power flows will be created. This project helps facilitate these new flow patterns. This projects facilitates the integration of large amounts of offshore wind generation connected to the north of the Netherlands by upgrading and expanding the Dutch transmission grid. | 150 | 150
349 | MaresConnect | MaresConnect is a 750MW HVDC VSC Interconnector between Great Britain and Ireland with three node connections; (i) Bodelwyddan (Wales), (ii) Maynooth (Dublin area, Ireland) and (iii) Bellacorick new node (Mayo area, Ireland). HVDC transmission will be made directly between Bellacorick and Bodelwyddan with a tapped connection at Maynooth. MaresConnect is an integral part of the MARES project, which aims to integrate 1,750MW of new RES and 6GWh of PHES in Mayo in the west of Ireland to the GB and SEM networks as well as provide increased interconnector capacity and voltage stability. | GB ;IE | 2025 | 2 | True | False | FALSE |  | Infrastructure to tackle a Need identified by one of the European ITEG indicators referring to the 15% interconnection target for 2030: 1. Reduce the price differential between EU countries to below 2EUR/MWh. 2. Contribute to pushing ratio between nominal transmission capacity and installed RES capacity past 30%. 3. Contribute to pushing ratio between nominal transmission capacity and peak load past 30%. Infrastructure to improve system flexibility and stability e.g. improve system or local ramp rate, improve transient stability or RoCoF to meet system Needs. Contribution to the power system's operational flexibility by controlling power flows and optimizing use of existing infrastructure Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | The European Commission Expert Group on Electricity Interconnection Targets recommends an increased threshold of interconnection capacity of at least 30% of installed renewable generation capacity by 2030 to ensure adequate export capacity for the continued development of renewable generation in Member States and is of particular relevance to IE wind potential IoSN report 2020 pages 42-44 ; RegIP NS 2020 ; MAF 2019; IoSN report 2020: Appendix Fig 15, 16; Regional Investment Plan: Fig 3.13; Regional Investment Plan CCE 2017: section 5.1; IoSN report 2020: Appendix Fig 15 & 16; IoSN Report 2020 (Appendix); Regional Investment Plan CSE 2020 (Ch. 3); Regional Investment Plan CSE 2017 (Ch. 5);IoSN main report (chapter 5) IoSN report 2020 pages 42-44 ; RegIP NS 2020 ; MAF 2019; IoSN report 2020: Appendix Fig 15, 16; Regional Investment Plan: Fig 3.13; Regional Investment Plan CCE 2017: section 5.1; IoSN report 2020: Appendix Fig 15 & 16; IoSN Report 2020 (Appendix); Regional Investment Plan CSE 2020 (Ch. 3); Regional Investment Plan CSE 2017 (Ch. 5);IoSN main report (chapter 5) The Ireland Climate Action Plan 2019 ‘to tackle climate breakdown’ sets The plan sets out a roadmap to 2030, which in electricity terms, primarily involves an primarily involves an Increased reliance on renewables from 30% to 70% adding 12GW of renewable energy capacity | 750 | 750
350 | South Balkan Corridor | This project consists of three investments: one 400 kV OHL Bitola(MK)- Elbasan(AL), and two 400 kV SS Ohrid and Kumanovo, in Macedonia. The interconnection contributes to increasing the transmission capacity in the East-West direction. The mentioned two SS-s will increase the security of supply in the SouthWest part of the FYR of Macedonia. Construction of 400 kV OHTL interconnection from SS Bitola 2 to Macedonian/Albanian border and SS 400/110 kV Ohrid 400 kV interconnection transmission line Bitola (Macedonia) - Elbasan (Albania) is the last part of the implementation of the Corridor 8 in the context of creating a corridor East-West power transmission corridor between Bulgaria, Macedonia, Albania and Italy. | AL ;MK | 2020 | 4 | True | True | FALSE |  |  |  | 500 | 500
375 | Lienz (AT) - Veneto region (IT) 220 kV | Reconstruction of the existing 220kV-interconnection line between Lienz and Veneto Region (IT). The project includes the adjustment of power regulation devices. Due to an update of the list of cross-border projects interconnecting Italy with other Member States within 2020, the 2020 interconnection ratio of Italy has been updated accordingly (from previous value of 9% computed by ENTSO-E in TYNDP 2018 to roughly 8%). As the Interconnection level of 10% will not be reached by 2020, Italy is requested to investigate options of further interconnections. | AT ;IT | 2027 | 2 | True | False | FALSE |  | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment Infrastructure to address system adequacy deficiencies and/or mitigate the risk of power failures. Infrastructure to tackle a Need identified by one of the European ITEG indicators referring to the 15% interconnection target for 2030: 1. Reduce the price differential between EU countries to below 2EUR/MWh. 2. Contribute to pushing ratio between nominal transmission capacity and installed RES capacity past 30%. 3. Contribute to pushing ratio between nominal transmission capacity and peak load past 30%. | This project contributes to lowering the price differentials between Italian market zones and Austria This project will improve the integration of italian RES generation This project will contribute to reduce system adequacy deficiencies by increasing transmission capacity. This project helps Italy to reach the 15% interconnection target by 2030. | 500 | 500
376 | Refurbishment of the 400kV Meliti(GR)-Bitola(MK) interconnector | The project aims at the reconductoring of the already existing 400kV interconnection line between Meliti (GR) and Bitola (MK), in order to increase transfer capacity between the power systems of Greece and North Macedonia. | GR ;MK | 2036 | 1 | True | False | FALSE |  | Infrastructure to tackle a Need identified by one of the European ITEG indicators referring to the 15% interconnection target for 2030: 1. Reduce the price differential between EU countries to below 2EUR/MWh. 2. Contribute to pushing ratio between nominal transmission capacity and installed RES capacity past 30%. 3. Contribute to pushing ratio between nominal transmission capacity and peak load past 30%. Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. | Project implementation will contribute to a further improvement of the following ITEG indicators: 2. pushing ratio between nominal transmission capacity and installed RES capacity past 30% The TYNDP-2020 IoSN studies indicate a need of NTC increase (NT2030 +1000MW, NT2040 +500MW) for the GR-MK interconnection. Replacing existing OH line conductors (2xACSR 490/65 1920 A/1330 MVA) with new ones of higher ampacity (2xCTC_Cardinal/ACCC/TW/ 680mm2) is thus justified | 500 | 500
377 | Upgrade BE-NL interconnector VanEyck-Maasbracht | This study envisions an upgrade of the existing interconnector VanEyck-Maasbracht between Belgium and the Netherlands making use of PSTs and/or HTLS technology.The study will determine the appropriate implementation option and timing, taking into account - The already planned upgrade of the Zandvliet-Rilland interconnector on the BE-NL border (see project 262) - The synchronisation with project study to upgrade interconnection DE-NL, also currently under consideration (see project 256) Project motivation: A need has been identified to further develop interconnection capacity on the BE-NL border, hereby alleviating VanEyck-Maasbracht as bottleneck. This project effectively increases the degree of interconnectivity between the Belgian and Dutch bidding zone. The possibility of higher market exchanges between these two bidding zones leads to a higher price convergence in more hours of the year and reduces therefore the price differentials. RES integration implies higher flows in the meshed AC-grid and thus increases the need for cross border transmission capacity. This project satisfies this need in a cost-efficient manner. This project is likely to increase the potential for imbalance netting & reserve sharing due to increased remaining available margins of the cross border transmission capacity. PSTs will also help to balance the flows over the different cross border lines of the Belgian Dutch interconnection. Based on the above, the project directly contributes to the 2030 interconnection criteria. | BE ;NL | 2030 | 1 | True | False | FALSE |  | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to address system adequacy deficiencies and/or mitigate the risk of power failures. Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | This project increases the degree of interconnectivity between the Belgian and Dutch bidding zones. The possibility of higher market exchanges between these two bidding zones leads to a higher price convergence in more hours of the year and reduces therefore the price differentials. This project has an important adequacy contribution due to decreasing figures of installed conventionals (bad market conditions) and considering the nuclear phaseout in Belgium. Phase shifting transformers will help to balance the flows over the different cross border lines of the Belgian Dutch border. RES integration implies higher flows in the meshed AC-grid and thus increases the need for cross border transmission capacity. This project satisfies this need in a cost-efficient manner. | 1000 | 1000
378 | Transformer Gatica | New tranformer 400/220 kV in existing Gatica subestation, with potential impact in cross border values | ES | 2025 | 2 | False | True | FALSE |  |  |  | - | -
379 | Uprate Gatica lines | Uprate of the following 400kV lines that reach Gatica subestation : Gatica-Gueñes, Gatica-Amorebieta-Ichaso and Gatica-Azpeitia. This internal project has influence in the exchange capacity values between France and Spain, and it is directly related to the P16 Biscay Gulf. | ES | 2025 | 1 | False | True | FALSE |  |  |  | - | -
1034 | HVDC corridor from Northern Germany to Western Germany | Project 1034 consists of two new HVDC cable from Heide/West to Polsum and from Wilhelmshaven to Uentrop. The HVDC have a transfer capacity of 2 GW each. The project is a grid expansion project for low-loss transmission of high power over long distances from Northern Germany to the Ruhr-Area. Northern Germany is characterized by a large number of regenerative onshore and offshore energy sources which exceed the demand of Northern German loads. The Ruhr-Area, however, is a high-production region with large conventional generation capacity that has to be substituted by renewable generation capacity due to the German coal phase-out. | DE | 2030 | 2 | False | True | FALSE |  | Infrastructure to improve system flexibility and stability e.g. improve system or local ramp rate, improve transient stability or RoCoF to meet system Needs. Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | Reducing the redispatch leading to more flexibility and increasing the stability of the system. In critical grid situations, costly congestion management measures are taken to avoid overload of grid elements. The project will reduce the demand for re-dispatching, countertrading and curtailment of renewable energy producers by adding significant transmission capacity between the congested routes in the North-Western part of Germany integration of huge amounts of offshore and onshore wind. | 4000 | 4000
1039 | SE North-south long-term reinforcements | Replacement of ageing overhead lines and reactive measures in substations and series compensations in order to increase capacity between SE2 and SE3. | SE | 2040 | 1 | False | True | FALSE |  |  |  | 1000 | 1000
1040 | LirIC | LirIC is a new HVDC sub-sea interconnector between Scotland and Northern Ireland. LirIC is being developed to increase the level of interconnection between Scotland and Northern Ireland addressing a market need and resulting in welfare generation opportunities in GB and consumer benefit in Ireland. A second beneficial driver for the project is the alleviation of Ireland's synchronous generation constraint, where there is an imposed limit on the level of demand that can be met by wind. These two effects result in significant benefit for British exports to Ireland to exploit wholesale power price arbitrage and Irish exports to Britain to avoid wind curtailment. | GB ;IE | 2027 | 1 | False | True | FALSE |  | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to address system adequacy deficiencies and/or mitigate the risk of power failures. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment Infrastructure to tackle a Need identified by one of the European ITEG indicators referring to the 15% interconnection target for 2030: 1. Reduce the price differential between EU countries to below 2EUR/MWh. 2. Contribute to pushing ratio between nominal transmission capacity and installed RES capacity past 30%. 3. Contribute to pushing ratio between nominal transmission capacity and peak load past 30%. | LirIC will provide increased capacity between the iSEM and GB markets thereby converging the prices of these two regions With significant increases in wind generation expected in Scotland the increased capacity between Scotland and Northern Ireland will increase options for the System Operators to efficiently balance the systems enhancing security of supply and reducing the risk of power failures in both regions. The LirIC project will give access to wider markets for the increasing level of RES in Scotland. The project will therefore reduce congestion on the Scotland-England border thereby reducing the level of RES curtailment. LirIC will contribute towards the GB and iSEM interconnection targets of 15% and support reducing price differentials between the two markets. | 700 | 700
1041 | GREGY Interconnector | The GREGY interconnection project concerns the possibility to create a new energy highway within the Mediterranean Basin, between South East region of ENTSOE and South Eastern Mediterranean power systems by interconnecting Egypt and Greece. Rational behind the project is to establish a new interconnection between two large synchronous areas enabling series of benefits such as market coupling, enhanced security of supply (Adequacy, Flexibility, Stability) and socio-economic welfare. GREGY is also part of a bigger project including the construction of large wind farms (app. 3300MW) in order to exploit the high wind potential of Egypt, mainly on the Suez Gulf and bank sides of the Nile. Therefore, the project is expected to allow RES energy exports from Egypt to Greece at times of high RES generation and also vice versa contributing to a significant increase of participation of renewables in the energy mix and reduction of greenhouse emissions of the power sector. GREGY project consists of an HVDC interconnection from Wadi-El-Natroon (Egypt) to Attica area (Greece) of total length approximately 1373km and HVAC network connecting Egypt converter station to wind farms location (app. 640km). | EG ;GR | 2028 | 1 | True | False | FALSE |  | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to address system adequacy deficiencies and/or mitigate the risk of power failures. Infrastructure and/or market design to provide balancing flexibility (e.g. international pooling / sharing of reserves, coordinated development of reserve capacity) Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | GREGY establishes a high capacity connection route between southeast Europe and Egypt along with nearby power systems, enabling electricity trading. Therefore, it will constitute a critical asset towards coupling of power markets of EU with North Africa and the Middle East. GREGY interconnector will allow sharing of the need for back-up adequacy resources among the interconnected countries. The risk of power failures, even in severe incidents, can be significantly reduced, provided that the interconnector will be able to cover power deficit up to 3GW. GREGY interconnector will also enable access to new balancing sources for both power systems. High capacity of interconnection will permit trading of significant volumes of balancing and reserve services, increase flexibility and allow optimal operation of variable RES. GREGY is part of a bigger project including the construction of large wind power plants (approximately 3300 MW), so that the high wind potential of Egypt can be optimally exploited. | 3000 | 3000
1042 | Offshore wind integration | Integration of 700 MW off-shore wind farms in Baltic Sea near Lithuania coast. To connect offshore wind farms it will be necessary to strenghten western part of 330 kV network in Lithuania, build offshore platform in Baltic Sea and connect platform via 60-80 km AC or DC cable to planned Darbenai substation. | LT | 2030 | 1 | False | True | FALSE |  | Infrastructure to address system adequacy deficiencies and/or mitigate the risk of power failures. Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. | Connection of 700 MW offshore wind farms is supporting national strategy targets in Lithuania to significally increase generation from renewables. Connecting 700 MW offshore wind farms will accommodate future scenarios, by helping to reach decarbonisation targets and increase generation from renewable energy sources. | 700 | 700
1043 | Wahle-Mecklar | North-South transmission in Germany. AC links from Northern Germany towards the load centers of Bavaria and Baden-Württemberg | DE | 2024 | 4 | False | True | FALSE |  |  |  | 0 | 0
1046 | N-S Finland P1 stage 3 | This project consists of the sixth 400 kV overhead line (Nuojuankangas-Huutokoski) connecting North Finland to South Finland, new 400 kV lines Tuomela B - Nuojuankangas and Petäjävesi-Hikiä as well as reactive compensation measures to improve the voltage stability of the grid. The project is built to increase the North-South transmission capacity thus enabling the integration of new renewable and conventional generation in northern Finland. | FI | 2030 | 3 | False | True | FALSE |  | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment Infrastructure to improve system flexibility and stability e.g. improve system or local ramp rate, improve transient stability or RoCoF to meet system Needs. |  | 1000 | 1000
1047 | Emden-Eemshaven | Increase of the interconnection capacity between the Netherlands (Eemshaven) and Germany (Emden) by adding a new 380kV tranmission line. The project is planned as a combination of overheadline, onshore cable and sub sea cable. | DE ;NL | 2035 | 1 | True | False | FALSE |  |  |  | 1000 | 1000
1048 | Greece - Africa Power Interconnector (GAP Interconnector) | The project refers to the construction of a submarine DC transmission link of total capacity 2000MW (2x1000MW) interconnecting Egypt's North Mediterranean coast and Greece at the island of Crete. A new HVDC conversion station close to the existing thermal power plant of Atherinolakkos in South-East Crete will be the connection point to Greece. Crete interconnection with mainland Greece is already under way by the Greek TSO (IPTO) with the implementation works expected to be completed before 2030 (both AC and DC links). Moreover, the "Southern Aegean Interconnector" transmission project will provide another transmission route of the transfer capacity through the Aegean sea. The connection point in Egypt will be at its Northern coast located South of Crete, where the bulk of Egypt's electrical load and HV transmission grid infrastructure is located. All the aforementioned installations (converter stations, substations etc) will be of closed type using GIS technology. The proposed Greece - Africa interconnection project will provide energy stability to the Eastern Mediterranean Sea area as intercontinental energy transfers will be facilitated and generation adequacy of the region will be increased. | EG ;GR | 2028 | 1 | True | False | FALSE |  | Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment Infrastructure to address system adequacy deficiencies and/or mitigate the risk of power failures. | The proposed Greece - Africa interconnection project will provide energy stability to the Eastern Mediterranean Region as intercontinental energy transfers will be facilitated and generation adequacy of the region will be increased. Various future scenarios will be made eligible for testing and analysis between EU and non EU cross border flows. Energy transactions between Greece and Egypt through GAP Interconnector (HVDC cable) will lead to reduced price differentials between EU (Greece) and non-EU countries (Egypt). Certainly the increased interconnection capacity between Greece and Egypt provided via the development of GAP Interconnector shall lead to significant decrease of RES curtailments. The increased Interconnection capacity provided via the infrastructure of GAP Interconnector will enhance System Adequacy for both Power Systems (Greek - EU and Egyptian - Africa). Power failures will be mitigated in a more bulk interconnected grid. | 2000 | 2000
1049 | Cronos Energy Ltd | Cronos Energy Ltd (“Cronos”) is permitting a 1400MW DC Bipole VSC interconnector between England and Belgium. The project started in 2017 and has obtained a legally binding grid connection agreement with National Grid at Kemsley, Kent in the UK for rights to construct, connect and operate an interconnector. The management team of Cronos has a successful track record in developing and operating interconnectors and transmission projects as well as large-scale grid connected power stations in the UK and Europe and has been involved in over 40GW of transmission power station and interconnector projects in Europe. Our mandated technical advisor for electrical engineering, infrastructure and power systems is WSP Ltd, our mandated financial advisor is EY (Ernst & Young). The interconnector is expected to reach commercial operations in late 2026 and the permitting and construction timetables are attached in Microsoft Excel format. Cronos has commenced the planning and environmental work as well as having undertaken detailed work on the undersea cable route and onshore works. Cronos is committed to the project and has detailed knowledge of interconnector permitting, regulatory regimes, energy contracting, project financing and construction and operations including O&M. | BE ;GB | 2025 | 1 | True | False | FALSE |  |  |  | 1400 | 1400
1050 | Tarchon Energy Ltd | Tarchon Energy Ltd (“Tarchon”) is permitting a 1400MW DC Bipole VSC interconnector between England and Germany. The project started in 2017 and has obtained a legally binding grid connection agreement with National Grid at Corringham in the UK for rights to construct, connect and operate an interconnector. The management team of Tarchon has a successful track record in developing and operating interconnectors and transmission projects as well as large-scale grid connected power stations in the UK and Europe and has been involved in over 40GW of transmission power station and interconnector projects in Europe. Our mandated technical advisor for electrical engineering, infrastructure and power systems is WSP Ltd, our mandated financial advisor is EY (Ernst & Young). The interconnector is expected to reach commercial operations in late 2026 and the permitting and construction timetables are attached in Microsoft Excel format. Tarchon has commenced the planning and environmental work as well as having undertaken detailed work on the undersea cable route and onshore works. Tarchon is committed to the project and has detailed knowledge of interconnector permitting, regulatory regimes, energy contracting, project financing and construction and operations including O&M. | DE ;GB | 2028 | 1 | True | False | FALSE |  |  |  | 1400 | 1400
1051 | Aminth Energy Ltd | Aminth Energy Ltd (“Aminth”) is permitting a 1400MW DC Bipole VSC interconnector between England and Denmark. The project started in 2017 and has obtained a legally binding grid connection agreement with National Grid at Norwich Main in the UK for rights to construct, connect and operate an interconnector. The management team of Aminth has a successful track record in developing and operating interconnectors and transmission projects as well as large-scale grid connected power stations in the UK and Europe and has been involved in over 40GW of transmission power station and interconnector projects in Europe. Our mandated technical advisor for electrical engineering, infrastructure and power systems is WSP Ltd, our mandated financial advisor is EY (Ernst & Young). The interconnector is expected to reach commercial operations in late 2026 and the permitting and construction timetables are attached in Microsoft Excel format. Aminth has commenced the planning and environmental work as well as having undertaken detailed work on the undersea cable route and onshore works. Aminth is committed to the project and has detailed knowledge of interconnector permitting, regulatory regimes, energy contracting, project financing and construction and operations including O&M. | DK ;GB | 2028 | 1 | True | False | FALSE |  |  |  | 1400 | 1400
1052 | Lienz (AT) - Obersielach (AT) | The 380-kV-ring can be completed in Austria with the reinforcement of the Carinthia transmission grid. The advantages of a ring structure are only made possible by the project. Security of supply in Carinthia and Austria can be guaranteed in the long term. With the 380-kV-ring closure in the south, a redundant connection of the renewable energy feed-in centers in the east Austria (mainly wind and PV) and the load centers with the pumped storage power plants in the central Alpine region. The 380-kV-ring closure is essential for the grid integration of renewable energies and the Austrian Federal Government's climate and energy strategy, and its necessity will also be addressed in the Carinthian Government's 2018-2023 program. The project will also enable the development of additional transmission capacity to the neighboring countries | AT | 2030 | 2 | False | True | FALSE |  | Infrastructure to improve system flexibility and stability e.g. improve system or local ramp rate, improve transient stability or RoCoF to meet system Needs. Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. Contribution to the power system's operational flexibility by controlling power flows and optimizing use of existing infrastructure Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | Facilitation of capacities between RES and pump storages in Austria as well as optimisation of cross border flows. Enabling future developments (load/generation). Faclilitation and optimisation of pump storage connections in the western part of Austria and therefore increasing flexibility. Connecting RES with pump storages. | 500 | 500
1054 | Westtirol (AT) - Zell/Ziller (AT) | An Upgrade of the existing 220kV-line Westtirol (AT) - Zell-Ziller (AT) and the erection of an additional 220/380kV-transformer. | AT | 2027 | 2 | False | True | TRUE | 3.1.4 | Infrastructure to improve system flexibility and stability e.g. improve system or local ramp rate, improve transient stability or RoCoF to meet system Needs. Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. Contribution to the power system's operational flexibility by controlling power flows and optimizing use of existing infrastructure Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | Facilitation of capacities between RES and pump storages in Austria as well as optimisation of cross border flows. Enabling future developments (load/generation). Faclilitation and optimisation of pump storage connections in the western part of Austria and therefore increasing flexibility. Connecting RES with pump storages. | 600 | 600
1055 | Interconnection of Crete to the Mainland System of Greece | Crete is the largest electrically non-interconnected island system in Greece, representing a particular case, due to large size, rapid growth, remote location and large RES potential. The project aims to increase security of supply and improve stability issues of the island by its interconnection to the mainland system. It is expected to contribute to the reduction of the operation of oil-fired units that currently supply the island and in the long run to allow their progressive decommissioning, thus contributing to the reduction of production variable costs and greenhouse gas emissions. It will allow the full exploitation of local RES potential. The project shall ensure a more reliable and cost-effective supply of electricity to the island. This interconnection will be implemented in two phases. In Phase I Crete will be connected to Peloponnese with a 150 kV AC double circuit submarine cable interconnector of 2x200 MVA nominal transfer capacity. In Phase II Crete will be connected to Attica with a bipolar submarine HVDC-VSC link of 2x500 MW capacity transfer. The project in total contributes in achieving the EU-wide targets and policy objectives set in the 2030 climate and energy framework. | GR | 2022 | 4 | False | True | FALSE |  | Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment Infrastructure designed to offer more supply options to isolated areas Infrastructure to address system adequacy deficiencies and/or mitigate the risk of power failures. | The project will allow the full exploitation of local abundant RES potential, currently subject to limitations imposed by the autonomous operation. Crete is currently the largest electrically non-interconnected island system in Greece that operates in autonomous mode. The project will increase security of supply and improve stability issues for the electric system of the island, by its interconnection to the mainland system. Crete is the largest electrically non-interconnected island system in Greece, characterized by high annual consumption and load peak. Adequacy issues have been recognized, as several generation units have to be decommissioned or replaced according to EU Directives. The project ensures system adequacy by interconnecting the island to mainland | 800 | 800
1056 | Croatian south connection | Currently, the South of Croatia is connected with the rest of Croatia via the territory of the Republic only by one electric power line SS Komolac - SS Rudine - SS Ston - SS Ponikve - SS Blato with transmission capacities limited to 110 MVA by the transmission line between SS Komolac and SS Ston. The second 110 kV connection is between SS Opuzen and TS Ston and it goes through the territory of BA and is introduced into SS Neum (BA). The safe operation of that part of the power system is largely dependent on interconnections with BiH. The power systems of Croatia and Bosnia and Herzegovina are extremely well connected with a total of 21 interconnectors at 400, 220 and 110 kV voltage levels contributing to the safety of both countries. However, the shape of territory and transmission network of Croatia, the southernmost part of the Croatian power system is practically dependent on interconnections with BA. To ensure the security of supply and enable additional integration of RES in that area following investments are necessary: 1. SS 400 kV ZONE 5, 2. SS 400/220 kV ZONE 6, 3. OHL 2x400 kV ZONE 5 - ZONE 6, 4. OHL 2x220 kV ZONE 6 – Plat, 5. SS 220/110 kV Plat | HR | 2035 | 1 | False | True | FALSE |  |  |  | 0 | 0
1057 | HVDC CentraLink | 2GW HVDC Connection from northern Germany (North Sea area) to Baden-Württemberg (Großgartach area). A rapid increase of the installed RES capacities in the northern areas o Germany has already by far exceeded the local load expectations and created an additional demand for transmission capacities. The RES based Generation mostly located in the northern regions of Germany has to be connected with the load centers situated in the southern parts of the country. The relevance, as well as, the sustainability of this concept project is directly correlated with the further increase of the installed RES capacities in the northern Germany. As such the idea complies to the vision of North-South-Interconnectors created and pursued by EC. | DE | 2035 | 1 | False | True | FALSE |  | Infrastructure to improve system flexibility and stability e.g. improve system or local ramp rate, improve transient stability or RoCoF to meet system Needs. Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | The new HVDC transmission link enable a power transmission over long distances with lower losses and contribute to the improving of voltage stability and security of supply in the German power system. The further expansion of RES capacities in Germany, especially offshore wind, leads in critical grid situations to the overloads of internal grid elements. The project will create an efficient targeted connection between RES in northern Germany and load centres in southern Germany, which prevents potential bottlenecks in transmission routes. The HVDC transmission link will directly connect regions with high amount of RES and load centres in southern Germany, which enables a further integration of RES. This project will also contribute to energy transport from south to north in case when there is high solar radiation and little wind. | 2000 | 2000
1058 | HVDC Interconnector DE-CH | This concept project concerns an extension of German HVDC lines towards Switzerland via an additional HVDC link. It pursues an ultimate goal to realise a new HVDC N-S corridor connecting the load / generation capacities in the North Sea area with the ones installed in the Mediterranean sea region. | CH ;DE | 2040 | 1 | True | False | FALSE |  | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to improve system flexibility and stability e.g. improve system or local ramp rate, improve transient stability or RoCoF to meet system Needs. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | This project increases the degree of interconnectivity between the Germany and Switzerland and possibility of higher market exchanges, which lead to higher price convergence. The full controllability of the HVDC link between Germany and Switzerland will contribute to the voltage stability and security of supply, which can significantly increase the flexibility of power systems in both countries. The further expansion of RES capacities in Germany, especially offshore wind leads to increasing RES-curtailment in the coming decades. By increasing the transmission capacity between Germany and Switzerland, the alternative HVDC measure allows a higher export in hours of high RES infeed. | 1000 | 1000
1059 | Southern Italy | New 400 kV lines in Campania and in Calabria, affecting existing 400 kV substation. The link will remove grid constraints and congestions due to the new renewable installed capacity. | IT | 2030 | 3 | False | True | FALSE |  | Infrastructure to address system adequacy deficiencies and/or mitigate the risk of power failures. Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. Contribution to the power system's operational flexibility by controlling power flows and optimizing use of existing infrastructure | Increase of security of supply The new line will allow congestion reduction on the Central-Southern/Southern border, and the integration of the local renewable production. Increasing of the Social Economic Welfare and reduction of the ancillary market services, especially in case of failure of the existing line 380 kV Laino-Altromonte | 200 | 200
1061 | Reactive compensation for project 197 | Reactive compensation in substations to increase the transfer capacity from North to South Finland: installation of STATCOM(s), SVC(s) and/or shunt compensation. This investment was previously included within project 197 but has been set aside to abide with the CBA Guideline clustering rules. | FI | 2022 | 1 | False | True | FALSE |  | Infrastructrure improving voltage stability by offering reactive power controllability of converters by system operator(s) Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to improve system flexibility and stability e.g. improve system or local ramp rate, improve transient stability or RoCoF to meet system Needs. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment
1062 | Reactive compensation for project 1046 | Reactive compensation measures in substations to increase the transfer capacity from North to South Finland: installation of STATCOM(s), SVC(s) and/or shunt compensation. This project supports project 1046 by improving the voltage stability of the grid. Compensation probably needed in two or more locations/substations. | FI | 2029 | 1 | False | True | FALSE |  | Infrastructrure improving voltage stability by offering reactive power controllability of converters by system operator(s) Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to improve system flexibility and stability e.g. improve system or local ramp rate, improve transient stability or RoCoF to meet system Needs. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment
1063 | ZuidWest380 West | New 380 kV connection between Borssele and Rilland. This investment was previously clustered within project 346. | NL | 2022 | 4 | False | True | FALSE |  | Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. | This projects facilitates the integration of large amounts of offshore wind generation connected to the west coast of the Netherlands by upgrading and expanding the Dutch transmission grid. This project helps accommodate the new flow patterns as a result of increased cross-border flows and the new generation mix due to future connection of high volumes of RES
1066 | Bulgaria - Turkey | The project concerns the construction of a new AC 400kV interconnection Bulgaria - Turkey. The proposed interconnection line with a total length 150 km will connect Maritsa East 2 SS in Bulgaria and Vize Havza SS in Turkey. This project, together with the project for a new interconnection between Greece and Turkey, compose the project “East Balkan Corridor” that will contribute to increasing the cross -border transfer capacities between ENTSO-E countries and Turkey and address a system need, identified in ENTSO-E's System Needs study. The construction of the two interconnections will also improve the stability of the connection of a large electricity system such as the Turkish one to the unified electricity system of the countries of continental Europe. Furthermore the project will allow integration of more renewables to the grids, support the convergence of market price between the neighboring countries and thus will help the realization of clean energy package targets. | BG ;TR | 2036 | 1 | True | False | FALSE |  | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to tackle a Need identified by one of the European ITEG indicators referring to the 15% interconnection target for 2030: 1. Reduce the price differential between EU countries to below 2EUR/MWh. 2. Contribute to pushing ratio between nominal transmission capacity and installed RES capacity past 30%. 3. Contribute to pushing ratio between nominal transmission capacity and peak load past 30%. Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. | The project contributes in reducing high price differentials indicated between Turkey and Bulgaria in the future due to the generation shift, enabling lower and more balanced wholesale prices. Project implementation will enhance transmission capacity between Bulgaria and Turkey and thus will contribute to a further improvement of the 2nd ITEG indicator pushing ratio between nominal transmission capacity and installed RES capacity past 30% Constraints (e.g. congestion) occur in future scenarios where high flows are exchanged between Bulgaria and Turkey with the current grid. The project contributes in transfer capacity increase, thus minimizing congestion at the BG – TR border. | 1100 | 700
1067 | New AC 400 kV interconnection line Greece - Turkey | The project concerns the construction of a new AC 400kV interconnection Greece - Turkey. The proposed interconnection line with a total length 130 km will connect Nea Santa SS in Greece and Babaeski SS in Turkey. This project, together with the project for a new interconnection between Bulgaria and Turkey, compose the project “East Balkan Corridor” that will contribute to the increase of the cross-border transfer capacities between ENTSO-E countries and Turkey and address a system need, identified in ENTSO-E's System Needs study. The construction of the two interconnections will also improve the stability of the connection of a large electricity system such as the Turkish one to the unified electricity system of the countries of continental Europe. Furthermore the project will allow integration of more renewables to the grids, support the convergence of market price between the neighboring countries and thus will help the realization of clean energy package targets. | GR ;TR | 2036 | 1 | True | False | FALSE |  | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to tackle a Need identified by one of the European ITEG indicators referring to the 15% interconnection target for 2030: 1. Reduce the price differential between EU countries to below 2EUR/MWh. 2. Contribute to pushing ratio between nominal transmission capacity and installed RES capacity past 30%. 3. Contribute to pushing ratio between nominal transmission capacity and peak load past 30%. Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. | The project contributes in reducing high price differentials indicated between Turkey and Greece in the future due to the generation shift, enabling lower and more balanced wholesale prices. Project implementation will enhance transmission capacity between Greece and Turkey and thus will contribute to a further improvement of the 2nd ITEG indicator pushing ratio between nominal transmission capacity and installed RES capacity past 30%. Constrains (e.g. congestions) occur in future scenarios where high flows are exchanged between Greece and Turkey with the current grid. The project contributes in transfer capacity increase, thus minimizing congestions at the GR – TR border. | 600 | 600
1068 | LaSGo Link | LaSGo Link is a new multi terminal HVDC sub-sea interconnector project linking Sweden, the Island of Gotland and Latvia. The project consists of two sections: a 700MW internal grid reinforcement between the Swedish mainland and the island of Gotland and a 500MW cross border connection between the island of Gotland and Latvia. LaSGo Link is being developed to increase grid capacity to Gotland and increase the level of cross border capacity in the Baltic Sea region. This will meet the current challenge of security of supply experienced in this region and therefore support industry and the further growth of wind power in the Gotland region. The cross border element of the project will provide further routes to market for generation thereby reducing internal grid congestion in Sweden and providing socio-economic benefit to both Sweden, Latvia and the interconnected markets in the Baltic Sea region. | LV ;SE | 2036 | 1 | True | False | FALSE |  | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to address system adequacy deficiencies and/or mitigate the risk of power failures. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment Infrastructure to tackle a Need identified by one of the European ITEG indicators referring to the 15% interconnection target for 2030: 1. Reduce the price differential between EU countries to below 2EUR/MWh. 2. Contribute to pushing ratio between nominal transmission capacity and installed RES capacity past 30%. 3. Contribute to pushing ratio between nominal transmission capacity and peak load past 30%. | The new cross border capacity will give lower cost generators in Sweden access to wider markets, reducing the cost of power in Latvia and converging prices in the region. LaSGo Link will mitigate current grid deficiencies and support the connection of offshore wind in the seas around the island of Gotland. Furthermore, the project will reduce current security of supply issues that are limiting industrial expansion on the island with increased access to decarbonised energy. The multi-terminal design of LaSGo Link improves the capital efficiency and operational security of connecting future offshore wind around the island of Gotland directly to the markets of Sweden and Latvia. The project will support reducing price differentials in the Baltic region and support the expansion of wind generation around the island of Gotland contributing to the 30% RES capacity target.
1074 | Pannonian Corridor | The new 400 kV line connecting Serbian and Hungarian transmission systems, initially considered to connect SS Subotica 3 (RS) and SS Sándorfalva (HU). This is, however, not definitely decided, as the bilaterally developed Pre-Feasibility Study is expected to be done in 2021. This Study will provide much clearer insight into the situation in the area of interest and suggest the optimal substations that should be connected by the new line. Also, this project includes strengthening the North-to-South transmission corridor in Serbian system, by building two new 400 kV lines: SS Sombor 3 – SS Srbobran and SS Srbobran – SS Sremska Mitrovica 2. This is also deemed necessary, as numerous calculations have indicated that the new tie-line may not affect the NTC value enough if it is not accompanied by the two mentioned internal lines. The project can, alongside covering the needs seen in IoSN report, also be seen as a response to the ever-higher requests for integration of renewable sources in the Bačka region, while simultaneously strongly enhancing the security of supply and reliability of the transmission systems' operation in the included countries. | HU ;RS | 2036 | 1 | True | False | FALSE |  | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to improve system flexibility and stability e.g. improve system or local ramp rate, improve transient stability or RoCoF to meet system Needs. Infrastructure and/or market design to provide balancing flexibility (e.g. international pooling / sharing of reserves, coordinated development of reserve capacity) Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | As the foreseen scope of the project envisages the new interconnection between Serbia and Hungary, it can be seen as another step towards the fully integrated energy market of the CSE region, leading to the noteworthy reduction of the price differentials between the EU and non-EU countries. The additional NTC, vouched for by the commissioning of this project, is expected to be a major asset in the field of system flexibility and stability, especially if the massive capacities of variable RES, predicted along the routes of its investments, are taken into consideration. As the fully integrated market represents one of the main goals set before the system development plans, the new interconnection enveloped by this project will certainly lead the systems of interest in the desired direction, characterized, among other facets, by the substantial balancing flexibility. Since the Bačka region, in the vicinity of the border between Serbia and Hungary, becomes more and more attractive for the investors in the wind plants each day, this project represents a guarantee that the energy evacuation from the newly built sources will happen reliably and safely. | 500 | 500
1077 | Crete-North Greece-North Macedonia-Bulgaria Interconnector | The Crete-North Greece-North Macedonia-Bulgaria Interconnector is a multiterminal HVDC interconnection project of 2000 MW connecting Crete, North of Greece (Thessaloniki), North Macedonia and Bulgaria. It will complement the project LEG1 (HVDC interconnection between Libya and Crete), reinforcing bidirectional electricity exchange between South-East Europe and North Africa. The project will have a DC voltage of 525 kV. VSC is preliminary chosen for converter technology because it is more favorable for power trading and has other advantages such as blackstart capacity and voltage stability support. This project will increase power exchange capacity between Greece, North Macedonia and Bulgaria and give to these countries access to solar energy from Libya, contributing to the achievement of the EC’s Green Deal 2030 objectives | BG ;GR ;MK | 2036 | 1 | True | False | FALSE |  | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to address system adequacy deficiencies and/or mitigate the risk of power failures. Capability for Black Start & Islanding Operation Infrastructrure improving voltage stability by offering reactive power controllability of converters by system operator(s) | ENTSO-E's System needs study finds a difference in electricity prices of 7.53 €/MWh between Greece and Bulgaria in 2040. Interconnecting these countries shall participate in reducing the price differential. VSC links have controllable AC output voltage and frequency, increasing grid stability VSC converters can be used to support the grid by mixing active and reactive power during stressed conditions VSC converter is available almost instantly after the blackout and includes blackstart capability and special modes of operation for islanded grids. The VSC converters will provide 500 MVar of reactive power and will be able to operate in STATCOM mode. | 2000 2000 | 2000 2000
1081 | LAG Interconnector (LAG) | LAG is a multiterminal HVDC interconnection project of 2000 MW connecting Libya (Tobruk) to the North-West of Greece (Arachthos) and subsequently to Albania (Tirana). It will reinforce bidirectional electricity exchange between South-East Europe and North Africa and help bridge the power deficit of Albania. LAG will have a DC voltage of 525 kV. VSC is preliminary chosen for converter technology because it is more favorable for power trading and has other advantages such as blackstart capacity and voltage stability support. This project will act as a power exchange platform but also give Albania and Greece access to RES electricity from Libya, contributing to the achievement of the EC’s Green Deal 2030 objectives. | AL ;GR ;LY | 2036 | 1 | True | False | FALSE |  | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to improve system flexibility and stability e.g. improve system or local ramp rate, improve transient stability or RoCoF to meet system Needs. Capability for Black Start & Islanding Operation Infrastructrure improving voltage stability by offering reactive power controllability of converters by system operator(s) | ENTSO-E's System Needs study finds a price difference of 8.7 €/MWh between Greece and Albania in 2040. Interconnecting these countries shall participate in reducing the price differential. VSC links have controllable AC output voltage and frequency, increasing grid stability VSC converters can be used to support the grid by mixing active and reactive power during stressed conditions VSC converter is available almost instantly after the blackout and includes blackstart capability and special modes of operation for islanded grids The VSC converters will provide 500 MVar of reactive power and will be able to operate in STATCOM mode. | 2000 2000 | 2000 2000
1082 | Sea-Socket | Sea-Socket - Connection of up to 700MW of additional offshore wind in Ireland. The Project aims to facilitate and leverage the substantial wind resources available on the West Coast of Ireland, estimated between 25 GWh – 27GWh. The project provides for innovative offshore grid infrastructure to include a high voltage substation platform centrally linking up to four offshore floating wind parks connecting a total of 700MW of new offshore wind. The size of the initial platform is 700-MW and will facilitate multiple connections points. The collected energy will be transmitted via 220kV subsea AC cables to onshore substation(s) located along the Shannon Estuary. Sea-Socket aims to mitigate the main the development constraints for the deployment of offshore wind capacity by efficiently reducing investment costs, the impact on the environment and streamlining the permitting process to connect new offshore generation facilities to the grid for use and export to other markets in the EU. Sea-Socket can make a substantial contribution to facilitating RES integration, and potentially supporting the realisation of emerging industrial opportunities in the production of hydrogen using offshore wind resources. | IE | 2036 | 1 | False | True | FALSE |  | Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment Infrastructure to reduce price differentials between EU and/or non-EU countries | The Project aim is to deliver high volumes of RES by the deployment of innovative offshore grid infrastructure (i.e. a floating substation/connection platform) to exploit the significant wind resources on the west coast of Ireland. The use of innovative and emerging floating technologies will enable the cost-efficient connection of multiple wind parks and reduce project constraints in fully realising Ireland’s wind resources for use and export to EU Member States. The Project will enable and deliver up to 700MW of floating offshore wind capacity in Ireland for export to other EU countries utilising existing and new interconnection (EWIC and PCIs North-South Line, Greenlink 286, Celtic 107 and storage PCI Silvermines Hydro 2.29). It will support the price differentials and trading capabilities between EU countries. | 700 | 700