## Sheet 2
TYNDP 2020 Transmission projects - General information on transmission investments | [6 empty] | Technical characteristics of the investment | [5 empty] | Costs of the investment |  |  | CBA indicators at investment level - Qualitative Stability Indicators |  |  | Residual environmental impact |  |  | Residual social impact |  |  | Other residual impact
Investment number | Investment Name | This investment belongs to project number… | Description of the investment | Commissioning Year | Status ID 1 : Under Consideration, 2 : In Planning but not permitting, 3 : In permitting, 4 : Under Construction | Progress of the investment since TYNDP2018 | Type of Element | Substation From | Substation To | Technology | Type of HVDC | Total route length (km) | Estimated CAPEX (MEUR) | Estimated OPEX (MEUR) | Cost Uncertainty Range | Transient stability | Voltage stability | Frequency stability | Distance (km) | Type of sensitivity | Additional information | Distance (km) | Type of sensitivity | Additional information | Other residual impact
1004 | 330kV OHL Paide-Sindi (L346) | 170 | Reinforcement of existing 330 kV OHL between Paide and Sindi 330 kV substations in Estonia. Old line will be replaced with new towers and wires of 3x400 mm2 in phase. The thermal capacity of the line is planned 1143 MVA. The investment is also a backbone for Baltics Synchronization with CE (project nr 170). | 2025 | 1 | Cancelled | ACTransmissionLine | Sindi | Paide | AC | None | 76 | 15 | 0.04 | +5%, - 5% | ++ | ++
1235 | Conceptual project | 233 | No details about the required network are known yet | 2027 | 1 | Delayed | ACTransmissionLine | - | - | AC | None | 0 | 75 | 1.125 | 10% | ++ | ++
1430 | TuNur AC | 283 | 400 kV AC underground cables from the HVDC converter in Montalto to Terna’s 400 kV station in Montalto. CAPEX includes 2 circuit breaker bays within Terna’s station. | 2026 | 1 | Delayed | ACTransmissionLine | Montalto di Castro (IT) VSC HVDC - 400 kV AC +/- 500 kV DC – 2x 1GW | Montalto di Castro (IT) Terna station 400 kV AC | AC | None | 2 | 16 | 0.04 | 8% of the overall project cost as exact length is not yet confirmed, it being understood that the impact of the short AC cable on the overall project will be negligible. | ++ | ++ | [7 empty] | TuNur DC: Job Creation - Creation of numerous qualified jobs in Tunisia for the construction and O&M of the land lines and HVDC converters
1694 | New 330 kV OHL Darbenai-Musa | 1042 | New 330 kV OHL Darbenai-Musa | 2030 | 1 | Delayed | ACTransmissionLine | Darbnai | Muša | AC | None | 170 | 66 | 0.143 | +5%, - 5%
1695 | New 330 kV OHL Panevezys-Musa | 1042 | New 330 kV OHL Panevežys-Muša | 2030 | 1 | Delayed | ACTransmissionLine | Panevežys | Muša | AC | None | 72 | 21.6 | 0.047 | +5%, - 5%
1270 | Baczyna-Zielona Góra | 229 | Indentation to the one circuit of 400 kV line Baczyna - Plewiska (construction 40 km new 400 kV line from new substation Zielona Góra to the point of indentation). Creating new route 400 kV Baczyna - Zielona Góra. | 2035 | 1 | Investment on time | ACTransmissionLine | Baczyna-Plewiska indentation | Zielona Góra | AC | None | 40 | 20 | 0.057 | 9% | ++ | ++
1271 | Zielona Góra - Plewiska | 229 | Indentation to the one circuit of 400 kV line Baczyna - Plewiska (construction 40 km new 400 kV line from new substation Zielona Góra to the point of indentation). Creating new 400 kV route Zielona Góra - Plewiska. | 2035 | 1 | Investment on time | ACTransmissionLine | Zielona Góra | Baczyna-Plewiska indentation | AC | None | 40 | 20 | 0.057 | 9% | ++ | ++
1282 | 380 kV Grid Reinforcement Beznau - Tiengen | 231 | This projects helps to increase the cross border capacity between Switzerland and Germany by upgrading an existing line from 220 kV to 380 kV including internal reinforcements. | 2030 | 1 | Investment on time | ACTransmissionLine | Beznau (CH) | Tiengen (DE) | AC | None | 11 | 58 | 0.304 | 10% | ++ | ++
1276 | Upgrading of existing 220 kV line between SS Dakovo (HR) and TPP Tuzla (BA) to 400 kV line | 241 | The project necessity stems for the need to increase the target transfer capacity between HR and BA in order to accommodate market integration and exploitation of RES, according to the results by the Common Planning Studies based on TYNDP2014 Vision 4. | 2033 | 1 | Investment on time | ACTransmissionLine | Dakovo | Tuzla | AC | None | 91 | 26 | 0.033 |  | ++ | ++
1277 | Upgrading of existing 220 kV line between SS Dakovo (HR) and Gradacac (BA) to 400 kV line | 241 | The project necessity stems for the need to increase the target transfer capacity between HR and BA in order to accommodate market integration and exploitation of RES, according to the results by the Common Planning Studies based on TYNDP2014 Vision 4. | 2033 | 1 | Investment on time | ACTransmissionLine | Dakovo | Gradacac | AC | None | 46.2 | 14.07 | 0.018 |  | ++ | ++
1279 | New double 400 kV line between SS Dakovo and location Razbojiste | 241 | New double 400 kV line between SS Dakovo and location Razbojiste enables connection of planned 400 kV SS Dakovo to existing 400 kV line Zerjavinec - Ernestinovo | 2033 | 1 | Investment on time | ACTransmissionLine | Dakovo | Razbojiste | AC | None | 25 | 10.375 | 0.0133 |  | ++ | ++
1530 | Upgrading of existing 220 kV line between SS Gradacac (BA) and TPP Tuzla (BA) to 400 kV line | 241 | Upgrading of existing 220 kV line between SS Gradacac (BA) and TPP Tuzla (BA) to 400 kV line | 2032 | 1 | Investment on time | ACTransmissionLine | SS Gradacac (BA) | TPP Tuzla (BA) | AC | None | 47.8 | 13.7 | 0.0176 |  | ++ | ++
1269 | New 400 kV overhead line Sombor (RS) - Ernestinovo (HR) | 243 | The project necessity stems for the need to increase the transfer capacity between RS and HR in order to accommodate connection of RES and improve market integration, according to the results based on TYNDP2018 CBA. | 2035 | 1 | Investment on time | ACTransmissionLine | Ernestinovo | Sombor | AC | None | 70 | 19.04 | 0.0245 | 5% | ++ | ++
1050 | Van Eyck - Gramme: HTLS upgrade | 252 | Upgrade of this double-circuit axis to HTLS conductors. Note that recently installed conductors along this axis anticipated the future HTLS upgrade, they don't have to be further upgraded. | 2029 | 1 | Investment on time | ACTransmissionLine | Van Eyck | Gramme | AC | None | 90 | 140 | 0.4 | 25% | ++ | ++
1205 | HU-RO | 259 | New 120 km single circuit 400 kV OHL between Hungary and Romania (90 km on Hungarian and 30 km on Romanian side) in order to reach the market based target capacity resulted from the TYNDP 2016 Common Planning Studies based in V4 and TYNDP 2018 IoSN in DG2040 and GCA2040. Internal investments in Romania associated to the project are also included. | 2030 | 1 | Investment on time | ACTransmissionLine | Józsa | Oradea | AC | None | 120 | 200 | 0.818 |  | ++ | ++
1258 | Rüthi - Bonaduz/Mettlen | 263 | Integration of the new 380 kV tie-line Rüthi (CH) - Meiningen (AT) through optimisations between Rüthi and Mettlen, Rüthi and Bonaduz and the construction of a new 380 kV substation and a new 380/220 kV transformer in Rüthi. | 2035 | 1 | Investment on time | ACTransmissionLine | Rüthi | Mettlen & Bonaduz | AC | None | 1 | 71 | 0.35 | 10% | ++ | ++ |  | 0 | None None
1583 | Vorarlberg | 263 | Voltage increase of all existing lines to 380 kV (without an increase of the line cross-section) and 2 new 380/22'0 kV transformers in Bürs | 2035 | 1 | Investment on time | ACTransmissionLine | Rüthi | Border area (DE-AT) | AC | None | 1 | 300 | 1.5 | 10% | ++ | ++ |  | 0 | None
1008 | Study Lonny-Achene-Gramme | 280 | Installation of PST(s) and/or line capacity upgrade of Lonny-Achene-Gramme | 2030 | 1 | Investment on time | ACTransmissionLine | Lonny (FR) | Gramme (BE) | AC | None | 0 | 90 | 0.1 | 25%
1536 | Portile de Fier (RO) - Djerdap (RS) 2nd | 341 | Portile de Fier (RO) - Djerdap (RS) 2nd . Doubling the existing OHL 400 kV (1.5 km on Serbian (thermal limit 1800 A) and 0.5 km on Romanian( thermal limit 2192 A) Side) | 2030 | 1 | Investment on time | ACTransmissionLine | Portile de Fier | Djerdap | AC | None | 2 | 3.5 | 0.03 | 5% | ++ | ++
1538 | New OHL 400 kV WPP Cibuk - SS Belgrade West | 341 | """New OHL 400 kV WPP Cibuk - SS Belgrade West""" | 2030 | 1 | Investment on time | ACTransmissionLine | WPP Cibuk | Belgrade West | AC | None | 60 | 14 | 0.15 | 5% | ++ | ++
1561 | BE-NL interconnector: upgrade VanEyck-Maasbracht | 377 | Upgrade of existing interconnection between Van Eyck (BE) and Maasbracht (NL), by adding PST(s) and/or replacing existing conductors by HTLS. The study is to confirm the appropriate implementation option and phasing of this implementation also with respect to evolution of DE-NL interconnectors. | 2030 | 1 | Investment on time | ACTransmissionLine | VanEyck | Maasbracht | AC | None | 12 | 50 | 0.1 | 25% | ++ | ++
1675 | SE North-south Long-term reinforcements | 1039 | Reactive measures in substations and series compensations in order to increase capacity between SE2 and SE3. Replacement of ageing overhead lines that also will contribute to the increased capacity. The need for capacity is driven by RES integration in northern Sweden and nuclear decommission in southern Sweden. | 2040 | 1 | Investment on time | ACTransmissionLine | SE2 | SE3 | AC | None | 950 | 2500 | 1 | -0.1
1673 | Zielona Góra - Polkowice | 229 | Construction of new 2x400 kV line from new substation Zielona Góra to existing substation Polkowice | 2035 | 1 | New Investment | ACTransmissionLine | Zielona Góra | Polkowice | AC | None | 90 | 75 | 0.14 | 9 | ++ | ++
1674 | Zielona Góra - Eisenhuettenstadt | 229 | Construction of new crossborder 2x400 kV line between new substation Zielona Góra (PL) end existing substation Eisenhuettenstadt (DE) | 2035 | 1 | New Investment | ACTransmissionLine | Zielona Góra | Eisenhuettenstadt | AC | None | 80 | 65 | 0.13 | 9 | ++ | ++
1483 | Upgrade Obersielach (AT) - Podlog (SI) | 325 | upgrade from 220 kV to 380 kV | 2034 | 1 | New Investment | ACTransmissionLine | Obersielach (AT) | Podlog (SI) | AC | None | 70 | 210 | 0.5 | 10 | ++ | ++ |  | 4 | OtherNatureProtectionAreasUnderNationalLaw |  | 81 | OtherNatureProtectionAreasUnderNationalLaw
1498 | New CZ-SK 400 kV interconnector | 330 | This investment consists of single circuit 400 kV OHL Otrokovice (CZ) - Ladce (SK). | 2035 | 1 | New Investment | ACTransmissionLine | Otrokovice (CZ) | Ladce (SK) | AC | None | 78 | 83.2 | 0.37 | ±10% | ++ | ++
1559 | Refurbishment of the 400kV Meliti (GR)-Bitola (MK) interconnector | 376 | Reconductoring of the existing 400kV interconnection line Meliti (GR)-Bitola (MK) | 2036 | 1 | New Investment | ACTransmissionLine | Meliti (GR) | Bitola (MK) | AC | None | 35.512 | 5.625 | 0.215 | ±20% | ++ | ++
1593 | Uprate Gatica-Guenes | 379 | Uprate 400 kV Gatica-Guenes substation | 2025 | 1 | New Investment | ACTransmissionLine | Gatica | Guenes | AC | None | 38.8 | 0.22 | 0.0033 | 10% | ++ | ++
1595 | Uprate Gatica-Amorebieta-Ichaso | 379 | Uprate the 400 kV axis Gatica-Amorebieta-Ichaso | 2025 | 1 | New Investment | ACTransmissionLine | Gatica | Ichaso | AC | None | 69.12 | 1.65 | 0.02475 | 10% | ++ | ++
1597 | Uprate Gatica-Azpeitia | 379 | Uprate the 400 kV Gatica-Azpeitia line | 2025 | 1 | New Investment | ACTransmissionLine | Gatica | Azpeitia | AC | None | 57 | 0.31 | 0.00465 | 10% | ++ | ++
1723 | OHL 2x400 kV ZONE 5 - ZONE 6 | 1056 | Double 400 kV line connecting SS ZONE 5 and ZONE 6 | 2035 | 1 | New Investment | ACTransmissionLine | ZONE 5 | ZONE 6 | AC | None | 90 | 45 | 0.063
1724 | OHL 2x220 kV ZONE 6 – Plat | 1056 | Double 220 kV line connecting SS ZONE 6 and SS Plat | 2035 | 1 | New Investment | ACTransmissionLine | ZONE 6 | Plat | AC | None | 105 | 36.75 | 0.05145 | 10
1736 | 400kV OHL, Maritsa East 2 (BG) – Vize Havza (TR) | 1066 | New interconnection line BG-TR by a 150km single circuit 400kV OHL. | 2036 | 1 | New Investment | ACTransmissionLine | Maritsa East 2 (BG) | Vize Havza (TR) | AC | None | 150 | 60 | 1.2 | -0.1
1738 | New AC 400 kV interconnection line Greece - Turkey | 1067 | New AC 400 kV Overhead line Greece - Turkey | 2036 | 1 | New Investment | ACTransmissionLine | Nea Santa (GR) | Babaeski (TR) | AC | None | 130 | 32.55 | 0.64 | ± 10%
1742 | 400 kV OHL SS Subotica 3 – SS Sándorfalva | 1074 | New 400 kV interconnection OHL between SS Subotica (RS) and SS Sándorfalva (HU). This is the main investment of the project and a part of the new North-South corridor for energy transmission. | 2036 | 1 | New Investment | ACTransmissionLine | SS Subotica 3 | SS Sándorfalva | AC | None | 50.6 | 24.1 | 0.4 | 10
1743 | 400 kV OHL SS Sombor 3 – SS Srbobran | 1074 | New 400 kV OHL from existing substation Sombor 3 to existing substation Srbobran (both in Serbia). | 2036 | 1 | New Investment | ACTransmissionLine | SS Sombor 3 | SS Srbobran | AC | None | 80 | 19.5 | 0.26 | 5
1744 | 400 kV OHL SS Srbobran – SS Sremska Mitrovica 2 | 1074 | New 400 kV OHL from existing substation Srbobran to existing substation Sremska Mitrovica 2 (both in Serbia). | 2036 | 1 | New Investment | ACTransmissionLine | SS Srbobran | SS Sremska Mitrovica 2 | AC | None | 90 | 21.2 | 0.272 | 5
1224 | Uprate of Creys-St Vulbas | 253 | Uprate of the double circuit 400-kV line Creys - Saint Vulbas with HTLS | 2031 | 1 | Rescheduled | ACTransmissionLine | Creys (FR) | Saint Vulbas (FR) | AC | None | 21 | 45 | 0.5 | 10% | ++ | ++
1541 | Zwolle-Hengelo-Doetinchem-Dodewaard | 344 | Upgrade of existing 380kV circuits between Zwolle, Hengelo, Doetinchem and Dodewaard from 2* 2,5 kA to 2* 4kA circuits by replacing the conductors with HTLS conductors | 2040 | 1 | Rescheduled | ACTransmissionLine | Zwolle | Dodewaard | AC | None | 165 | 210 | 2.1 | 10% | ++ | ++
1687 | AC Overhead Line 1 (Ras Ghareb-Nile West) | 1041 | AC 500KV interconnection line (double circuit OHL) which connects Wind Farms of Ras Ghareb to Nile West point | 2028 | 1 |  | ACTransmissionLine | Ras Ghareb Wind Farms Substation | Nile West | AC | None | 420 | 232 | 0.772 | 10
1690 | AC Overhead Line 2 (Nile West-Wadi El Natroon EHV) | 1041 | AC 500KV Interconnection Lines (two double-circuit OHLs) which connect Nile West Point with Wadi El Natroon EHV Center | 2028 | 1 |  | ACTransmissionLine | NILE WEST POINT | WADI EL NATROON | AC | None | 220 | 243 | 0.814 | 10
1107 | 2nd interconnecter between Belgium and Germany | 225 | This investment item envisions the possibility of a second 1 GW HVDC interconnection between Belgium and Germany. Subject to further studies. | 2035 | 1 | Delayed | DCTransmissionLine | Gramme (BE) | Dahlem (DE) | DC | None | 150 | 600 | 4.8 | 20% | ++ | ++
1722 | HVDC Line C3 | 1057 | New HVDC line to integrate the additional wind power capacity in the northern Germany in order to supply it to the load centers and storage units in the southern parts of the country. | 2035 | 1 | New Investment | DCTransmissionLine | Schleswig Holstein area | Baden-Württemberg area | DC | Bipolar | 700 | 5600 | 44.8 | ±20%
1726 | HVDC Line DE-CH | 1058 | The concept of extending German HVDC-Lines towards Switzerland and Italy offers a further potential to realize a new N-S HVDC corridor. Large developments of variable wind and photovoltaic power, coal and nuclear phaseout, mainly gas-based thermal generation, and the pump storage potentials in the Alps are the main drivers of power system evolution that will challenge the future transmission system in central southern Europe. | 2040 | 1 | New Investment | DCTransmissionLine | Wendlingen (DE) | Mettlen (CH) | DC | None | 0 | 2500 | 20 | ±20%
1749 | Greece Albania | 1081 | The HVDC interconnector will link Greece to Albania with XLPE underground cables or OHL, and use VSC converters. | 2036 | 1 | New Investment | DCTransmissionLine | Arachtos | Elbasan | DC | Bipolar | 180 | 1100 | 30 | 20
1682 | Wadi El Natroon - Acharnes HVDC | 1041 | Wadi El Natroon - Acharnes HVDC Link. This investment includes two LCC converter stations at both ends of the bipolar 600kV HVDC link along with the grounding electrodes. The interconnection circuits consist of approximately 500km of overhead HVDC lines (ACSR/PLOVER), approximately 30km length of underground cables (Al 1800mm2) and approximately 843km of submarine Cables (Cu 1000mm2, Al 1300mm2). | 2028 | 1 |  | DCTransmissionLine | Wadi El Natroon | Acharnes | DC | Bipolar | 1373 | 3525 | 76.186 | 10 |  |  |  | 83 | HabitatsDirective |  | 18.5 | HabitatsDirective
1747 | Northern Greece-North Macedonia | 1077 | The project will have a DC voltage of +/-525 kV. It will transmit 2000MW through bipolar HVDC cables. Converter technology is VSC. | 2036 | 1 |  | DCTransmissionLine | Thessaloniki | Dubrovo | DC | Bipolar | 110 | 800 | 30 | 20
1748 | North Macedonia-Bulgaria | 1077 | The project will have a DC voltage of +/-525 kV. It will transmit 2000MW through bipolar HVDC cables. Converter technology is VSC. | 2036 | 1 |  | DCTransmissionLine | Dubrovo | Ch. Mogila | DC | Bipolar | 170 | 1100 | 30 | 20
1433 | Southern Aegean Interconnector | 293 | Connection Wind Farms with AC Substations at Levitha and Syrna | 2025 | 1 | Investment on time | OffshoreACTransmissionCable | Levitha | Syrna | AC | None | 81 | 150 | 7 | 5% | ++ | ++
1434 | Southern Aegean Interconnector | 293 | AC Submarine cable to connect Kinaros substation to the AC side of Levitha Substation | 2024 | 1 | Investment on time | OffshoreACTransmissionCable | Kinaros | Levitha | AC | None | 14 | 30 | 1 | 5% | ++ | ++
1435 | Southern Aegean Interconnector | 293 | HVAC Submarine cable to connect Kandeliousa OffsHore Wind Farm HV substation to Syrna HV Subsation | 2025 | 1 | Investment on time | OffshoreACTransmissionCable | Kandeliousa | Syrna | AC | None | 34 | 80 | 6 | 5% | ++ | ++
1436 | Southern Aegean Interconnector | 293 | HVAC Submarine cable connect Kandeliousa offshore Wind Farm HV substation to Pergousa HV Substation | 2025 | 1 | Investment on time | OffshoreACTransmissionCable | Kandeliousa | Pergousa | AC | None | 14 | 40 | 2 | 5% | ++ | ++
1704 | Southern Aegean Interconnector | 293 | HVAC Submarine cable connecting Levitha offshore Wind Farm HV substation to Dodecanese (Kos & Rhodes HV Substation) | 2026 | 1 | New Investment | OffshoreACTransmissionCable | Levitha | Kos - Rhodes | AC | None | 170 | 330 | 10 | 5% | ++ | ++
1691 | Emden-Eemshaven | 1047 |  | 2035 | 1 | New Investment | OffshoreACTransmissionCable | Emden | Eemshaven | AC | None | 31 | 200 | 1.6 | -0.1
1378 | TuNur DC | 283 | TuNur DC consists in a +/- 500 kV DC overhead line in Tunisia from the CSP plant to the shoring point, submarine cables from the Tunisian Northern coast to Montalto di Castro in Italy and VSC HVDC converter stations at both terminal points. | 2026 | 1 | Delayed | OffshoreDCTransmissionCable | Rejim Maatoug (TN) VSC HVDC - 400 kV AC +/- 500 kV DC – 2x 1GW | Montalto di Castro (IT) VSC HVDC - 400 kV AC +/- 500 kV DC – 2x 1GW | DC | Bipolar | 1270 | 2680 | 41 | 8% | ++ | ++ |  | 1 | OtherNatureProtectionAreasUnderNationalLaw |  |  |  |  | TuNur DC: Job Creation - Creation of numerous qualified jobs in Tunisia for the construction and O&M of the land lines and HVDC converters
934 | Nautilus: 2nd interco UK - BE | 121 | This investment item envisions the possibility of a second HVDC connection between UK and a Belgian 380kV substation near the coast. Subject to further studies | 2028 | 1 | Investment on time | OffshoreDCTransmissionCable | Leiston (UK) | TBD (BE) | DC | None | 180 | 900 | 8 | 30% | ++ | ++ | + |  | None
1016 | DKE-DE (Kontek 2) | 179 | New 600 MW HVDC subsea cable connecting DK2 and DE. Also called Kontek 2 | 2030 | 1 | Investment on time | OffshoreDCTransmissionCable | Ørslevvester (DKE) | Bentwisch (DE) | DC | None | 170 | 460 | 9 | 20% | ++ | ++ | [7 empty] | This information is not available as the project is on a very early phase.
1236 | DKE-PL-1 | 234 | The first HVDC connector between Denmark-East and Poland. The planned transmission capacity of the new connection is 600 MW. | 2033 | 1 | Investment on time | OffshoreDCTransmissionCable | Avedøre (DKE) | Dunowo (PL) | DC | Bipolar | 330 | 655 | 13 | 20% | ++ | ++
1255 | Interconnector GB-NL | 260 | Multi-purpose interconnector between GB and NL also connecting GB and NL windfarms. | 2030 | 1 | Investment on time | OffshoreDCTransmissionCable | TBD | TBD | DC | None | 0 | 850 | 6 | ±10% | ++ | ++ | +
1262 | Hansa PowerBridge II | 267 | Possible second HVDC cable interconnector between southern Sweden (Bidding area SE4) and Germany (50Hertz). This project candidate is driven by market based target capacities found in the Common Planning Studies by Regional Group Baltic Sea. | 2030 | 1 | Investment on time | OffshoreDCTransmissionCable | Hurva (SE4) | Guestrow (DE) | DC | None | 300 | 660 | 1 | -0.1 | ++ | ++ | +
1431 | Southern Aegean Interconnector | 293 | New DC link (2 converter SS + 245 km DC subm. cable) to connect 582MW of offshore WF generation to the mainland (Area of Athens and Crete Island) | 2024 | 1 | Investment on time | OffshoreDCTransmissionCable | Lavrio | Levitha | DC | None | 245 | 600 | 40 | 5% | ++ | ++
1432 | Southern Aegean Interconnector | 293 | Interconnection of the Crete Island to the Greek Mainland via Levitha converter station. | 2026 | 1 | Investment on time | OffshoreDCTransmissionCable | Levitha | Atherinolakkos Crete | DC | None | 250 | 600 | 40 | 5% | ++ | ++
1505 | Interconnection DKw to Power Link Island | 335 | HVDC connector including substations interfacing the Power Link Island and the Western Danish power system. | 2035 | 1 | New Investment | OffshoreDCTransmissionCable | "Endrup, DKw" | Power Link Island DKw | DC | None | 328 | 1310 | 4.3 | The Capex uncertainty range for this 525kV link covers -20% to +30%. This can be explained by the different costs which are registered for currently realized projects to connect offshore windfarms. This range can be explained by the project specific differences. Since there is no clarity on the project specifics in this phase of the project, the uncertainty range thereby reflects this. | ++ | ++
1506 | Interconnection NL Maasvlakte to Power Link Island | 335 | One of two HVDC connectors including substations interfacing the Power Link Island and the Dutch power system. | 2035 | 1 | New Investment | OffshoreDCTransmissionCable | Maasvlakte 380 kV | Power Link Island NL1 | DC | None | 360 | 1375 | 4.4 | The Capex uncertainty range for this 525kV link is -20% to +30%. This can be explained by the different costs which are registered for currently realized projects to connect offshore windfarms. This range can be explained by the project specific differences. Since there is no clarity on the project specifics in this phase of the project, the uncertainty range thereby reflects this. | ++ | ++
1507 | Interconnection NL Eemshaven to Power Link Island | 335 | One of two HVDC connectors including substations interfacing the Power Link Island and the Dutch power system. | 2035 | 1 | New Investment | OffshoreDCTransmissionCable | Eemshaven 380 kV | Power Link Island NL2 | DC | None | 290 | 1233 | 4.2 | The Capex uncertainty range for this 525kV link is -20% to +30%. This can be explained by the different costs which are registered for currently realized projects to connect offshore windfarms. This range can be explained by the project specific differences. Since there is no clarity on the project specifics in this phase of the project, the uncertainty range thereby reflects this. | ++ | ++
1508 | Interconnection DE (area of Brunsbüttel) to Power Link Island | 335 | One of three HVDC connectors including substations interfacing the Power Link Island and the German power system. | 2035 | 1 | New Investment | OffshoreDCTransmissionCable | German substation located in the area of Brunsbüttel (north of the Elbe) | Power Link Island DE1 | DC | None | 390 | 1639 | 5.3 | The Capex for the 640kVHVDC links are extrapolated from 525kV HVDC links and therefore are subject to the same uncertainty range. Furthermore, additional needed internal reinforcements that can have a fundamental impact on the costs have not yet been analysed. | ++ | ++
1509 | Interconnection DE (area of Oldenburg) to Power Link Island | 335 | One of three HVDC connectors including substations interfacing the Power Link Island and the German power system. | 2035 | 1 | New Investment | OffshoreDCTransmissionCable | German substation located in the area of Oldenburg | Power Link Island DE2 | DC | None | 400 | 1661 | 5.3 | The Capex for the 640kVHVDC links are extrapolated from 525kV HVDC links and therefore are subject to the same uncertainty range. Furthermore, additional needed internal reinforcements that can have a fundamental impact on the costs have not yet been analysed. | ++ | ++
1511 | Interconnection DE (area of Krümmel) to Power Link Island | 335 | One of three HVDC connectors including substations interfacing the Power Link Island and the German power system. | 2035 | 1 | New Investment | OffshoreDCTransmissionCable | German substation located in the area of Krümmel | Power Link Island DE3 | DC | None | 490 | 1860 | 5.6 | The Capex for the 640kVHVDC links are extrapolated from 525kV HVDC links and therefore are subject to the same uncertainty range. Furthermore, additional needed internal reinforcements that can have a fundamental impact on the costs have not yet been analysed. | ++ | ++
1677 | LirIC | 1040 | New HVDC VSC Monopole sub sea cable between Kilroot 275kV substation in Northern Ireland (TBC) and Hunterston 400kV sub station in Scotland (TBC) | 2027 | 1 | New Investment | OffshoreDCTransmissionCable | NI Kilroot 275kV (TBC) | GB Hunterston 400kV (TBC) | DC | Monopolar | 133 | 446 | 9.93 | 20
1709 | Greece Africa Power Interconnector | 1048 | 2 HVDC Subsea cables interconnecting the Northern coast of Egypt with the island of Crete at Atherinolakkos. At both connection points bipolar HVDC conversion stations will be constructed for the connection to the national HV grids. | 2028 | 1 | New Investment | OffshoreDCTransmissionCable | Atherinolakkos (Crete) | Mersa Matruh | DC | Bipolar | 450 | 1700 | 25 | 5%
1706 | Converter Stations & Subsea Cabling | 1049 | 1.4 GW HVDC electricity interconnector between UK and Belgium Voltage Source Converter (VSC)/Bipolar Grid connection point (substations name): Kemsley (UK) and near Zeebrugge (Belgium), exact substation location subject to grid study in Belgium. Total cable length (substation to substation) 230km (1km in UK and 30km in France) Two cables (XLPE) laid in a single trench Nominal voltage: ±525 kV Thermal limit (Imax): 1330 A Mvar capability range at terminals: 460 MVAr Bus-bar to bus-bar losses profile over MW range: 2.3% (33 MW) full load; 0% (0 MW) at zero load. The annual Availability is 98.1% availability, with 1.8% planned outages, and 0.1% forced outages. The maximum single failure according to the design is 1.4GW. The project will enable the reduction of CO2 emissions by substituting electricity from fossil fuels by generation from RES and nuclear power. There are no material anticipated environmental impacts during construction and operation. | 2025 | 1 | New Investment | OffshoreDCTransmissionCable | Kemsley | Zeebrugge | DC | Bipolar | 230 | 746 | 28 | 6 |  |  |  | 1 | MarinStrategyFrameworkDirective |  |  |  |  | No other residual impact
1707 | Converter stations and Subsea Cabling | 1050 | 1.4 GW HVDC electricity interconnector between UK and Germany Voltage Source Converter (VSC)/Bipolar Grid connection point (substations name): Corringham (UK) and near Emden (Germany), exact substation location subject to grid study in Germany. Total cable length (substation to substation) 610km (35km in UK and 25km in Germany) Two cables (XLPE) laid in a single trench Nominal voltage: ±525 kV Thermal limit (Imax): 1330 A Mvar capability range at terminals: 460 MVAr Bus-bar to bus-bar losses profile over MW range: 2.3% (33 MW) full load; 0% (0 MW) at zero load. The annual Availability is 98.1% availability, with 1.8% planned outages, and 0.1% forced outages. The maximum single failure according to the design is 1.4GW. The project will enable the reduction of CO2 emissions by substituting electricity from fossil fuels by generation from RES and nuclear power. There are no material anticipated environmental impacts during construction and operation | 2028 | 1 | New Investment | OffshoreDCTransmissionCable | corrignham | emden | DC | Bipolar | 610 | 1260 | 23 | 3%
1708 | Converter stations and Subsea cables | 1051 | 1.4 GW HVDC electricity interconnector between UK and Germany Voltage Source Converter (VSC)/Bipolar Grid connection point (substations name): Norwich Main (UK) and near Revsing (Denmark), exact substation location subject to grid study in Denmark. Total cable length (substation to substation) 610km (35km in UK and 25km in Germany) Two cables (XLPE) laid in a single trench Nominal voltage: ±525 kV Thermal limit (Imax): 1330 A Mvar capability range at terminals: 460 MVAr Bus-bar to bus-bar losses profile over MW range: 2.3% (33 MW) full load; 0% (0 MW) at zero load. The annual Availability is 98.1% availability, with 1.8% planned outages, and 0.1% forced outages. The maximum single failure according to the design is 1.4GW. The project will enable the reduction of CO2 emissions by substituting electricity from fossil fuels by generation from RES and nuclear power. There are no material anticipated environmental impacts during construction and operation. | 2028 | 1 | New Investment | OffshoreDCTransmissionCable | Norwich Main | Revsing | DC | Bipolar | 640 | 1151 | 28 | 6 |  |  |  | 0 | MarinStrategyFrameworkDirective
1740 | LaSGo Link - Gotland to Latvia | 1068 | New monopolar HVDC VSC monopole sub-sea cable running from a new substation in Gotland (TBC) to Grobina in Latvia (or Ventspils or a possible a new substation inbetween Grobina and Ventspils) (TBC). This investment consists of two VSC HVDC converter stations connected via two 320kV HVDC XLPE cables. | 2036 | 1 | New Investment | OffshoreDCTransmissionCable | New substation on Gotland (TBC) | Grobina (TBC) | DC | Monopolar | 195 | 511.5 | 8 | +/-15%
1741 | LaSGo Link - Sweden to Gotland | 1068 | New monopolar HVDC VSC monopole sub-sea cable running from the vicinity of Oskarshamn in mainland Sweden (TBC) to a new substation in Gotland (TBC). This investment consists of one HVDC VSC converter station connected via two 320kV HVDC XLPE cables to a Converter Station being built as part of the LaSGo Link Gotland to Latvia investment. | 2036 | 1 | New Investment | OffshoreDCTransmissionCable | Oskarshamn (TBC) | New substation on Gotland (TBC) | DC | Monopolar | 125 | 287.5 | 4 | +/-15%
1745 | Libya Greece | 1081 | The HVDC interconnector will link Libya to Greece with XLPE or MI submarine cables, and use VSC converters. | 2036 | 1 | New Investment | OffshoreDCTransmissionCable | Tobruk | Arachtos | DC | Bipolar | 1070 | 3400 | 30 | 20
1241 | Fenno-Skan 1 renewal | 239 | Replacement of the existing 400 kV HVDC cable interconnection between Finland and Sweden. Fennoskan 1 will be decomissioned at the same time with this project being commisioned, which reduces capacity between FI and SE3 by 400 MW while increasing SE2-FI by 800 MW. | 2035 | 1 | Rescheduled | OffshoreDCTransmissionCable | Hjalta (SE2) | Tuovila (FI) | DC | None | 200 | 488 | 0.75 | +/-15 % | ++ | ++
1437 | Britib | 296 | Interconnection project between South-West England (United Kingdom), Cordemais (France) and Basque Country (Spain) in a multiterminal VSC HVDC bipole configuration of +/- 500-600 kV with 3 inputs/outputs of 1800 MW each, and a mostly subsea route from Spain to Great Britain along the French coast of about 1330 km in total. | 2026 | 1 | Rescheduled | OffshoreDCTransmissionCable | Gatica/Hernani (Spain), Cordemais (France) and Langage/Indian Queens (United Kingdom) | Gatica/Hernani (Spain), Cordemais (France) and Langage/Indian Queens (United Kingdom) | DC | Bipolar | 1330 | 2040 | 20 | +/- 10% | ++ | ++ | +
1746 | Crete-Northern Greece | 1077 | The project will have a DC voltage of +/-525 kV. It will transmit 2000MW through bipolar HVDC cables. Converter technology is VSC. It will connect to LEG1 converter station of Linoperamata (Crete). | 2036 | 1 |  | OffshoreDCTransmissionCable | Linoperamata | Thessaloniki | DC | Bipolar | 600 | 1900 | 30 | 20
1504 | Power Link Island | 335 | Artificial island central in the North Sea (best location for the first hub is under investigation) with a 'copper plate' type electrical installation suitable to connect 12GW of HVDC systems to shore and up to 12GW of nearby offshore wind. The artificial island is large enough to host all equipment HVDC converters and O&M facilities. Reduction of the total system cost is essential to facilitate large scale offshore wind and interconnection capacity deployment and all options in design, installation and operation should be considered to further reduce cost, including the use of a power hub as an island. Realising a power hub as an island located centrally in the North Sea has been assessed to be technically feasible, based on - amongst others - bathymetry, extreme wind speed and hydraulic conditions (wave heights, surge levels, etc.) and geotechnical data. | 2035 | 1 | New Investment | OffshoreSubstation | 0 | 0 | AC | None | 0 | 2222 | 11 | The Capex uncertainty range for this asset is -20% to +30%. This can be explained by the different costs which are registered for currently realized projects to connect offshore windfarms. This range can be explained by the project specific differences. Since there is no clarity on the project specifics in this phase of the project, the uncertainty range thereby reflects this. | ++ | ++
1750 | Sea-Socket | 1082 | Floating substation platform facilitating 700-MW multiple offshore wind connections and transmitted via 220kV subsea AC cables to onshore substation(s) located along the Shannon Estuary | 2035 | 1 | New Investment | OffshoreSubstation | New substation connection to 400kV/220kV lines in the Shannon Estuary | Not applicable - offshore connection point at Sea-Socket Platform | AC | None | 40 | 375 | 12 | 25%
650 | BE-LUX-DE Long-Term perspective | 40 | The technical solution is subject to further studies | 2035 | 1 | Rescheduled | OnshoreACTransmissionCable | Aubange (TBC) | LUX-DE (TBC) | AC | None | 16 | 210 | 0.6 | 25% | ++ | 0
1272 | Zielona Góra | 229 | Construction of new substation 400/110 kV Zielona Góra to connect 400 kV lines : Baczyna - Zielona Góra, Zielona Góra - Plewiska, Zielona Góra - Eisenhuettenstadt (with installation of Phase Shifting Transformers), Zielona Góra - Polkowice | 2035 | 1 | Investment on time | OnshoreSubstation | Zielona Góra | n.a. | AC | None | 0 | 90.4 | 2.712 | 5% | ++ | ++
1278 | Upgrading existing 220 kV SS Dakovo to 400 kV | 241 | Upgrading existing 220 kV SS Dakovo to 400 kV enables connection between SS Dakovo (HR) and TPP Tuzla/Gradacac (BA) by 400 kV lines. | 2033 | 1 | Investment on time | OnshoreSubstation | Dakovo | Dakovo | AC | None | 0 | 11 | 0.0141 |  | ++ | ++
1531 | Upgrading existing 220 kV SS Gradacac (BA) to 400 kV | 241 | Upgrading existing 220 kV SS Gradacac (BA) to 400 kV | 2032 | 1 | Investment on time | OnshoreSubstation | SS Gradacac (BA) | SS Gradacac (BA) | AC | None | 0 | 7.9 | 0.01 |  | ++ | ++
1718 | SS 400 kV ZONE 5 | 1056 | New 400 kV substation interpolated in existing 400 kV line Konjsko - Mostar | 2035 | 1 | New Investment | OnshoreSubstation |  |  | AC | None | 0 | 8 | 0.0112 | 10
1719 | SS 400/220 kV ZONE 6 | 1056 | New 400 kV substation for connetion of new generation and increase of security of supply in the southern area near city of Ploce | 2035 | 1 | New Investment | OnshoreSubstation |  |  | AC | None | 0 | 17.5 | 0.0245 | 10
1725 | SS 220/110 kV Plat | 1056 | Construction of two addiotional OHL bays for connection of OHL 220 kV ZONE 6 - Plat | 2035 | 1 | New Investment | OnshoreSubstation | ZONE 6 | Plat | AC | None | 0 | 2 | 0.0028 | 10
1496 | PST Foretaille | 333 | Installation of two PSTs in Foretaille that control the flow on the Foretaille - Verbois 220 kV double line | 2031 | 1 | Investment on time | PhaseShiftingTransformer | Foretaille | Foretaille | AC | None | 0 | 35 | 0.18 | 10%
1225 | PST in Cornier | 253 | Phase Shifter Transformer in order to attract the flows and alleviate the congestion on the France-switzerland interconnection west of Lake Geneva. | 2031 | 1 | Rescheduled | PhaseShiftingTransformer | Cornier (FR) | Cornier (FR) | AC | None | 0 | 15 | 0.1 | 10% | ++ | ++
1729 | Reactive compensation | 1061 | Reactive compensation in substations to increase the transfer capacity from North to South Finland: installation of STATCOM(s), SVC(s) and/or shunt compensation. | 2022 | 1 |  | ReactiveCompensationDevice | North Finland | South Finland | AC | None | 0 | 20 | 0.1 | +/- 100%
1730 | Reactive compensation | 1062 | Reactive compensation measures in substations to increase the transfer capacity from North to South Finland: installation of STATCOM(s), SVC(s) and/or shunt compensation. | 2029 | 1 |  | ReactiveCompensationDevice | North Finland | South Finland | AC | None | 0 | 30 | 0.1 | +/- 100%
1537 | New SS 400/110 kV Belgrade West | 341 | New SS 400/110 kV Belgrade West | 2030 | 1 | Investment on time | Transformer | Belgrade West | Belgrade West | AC | None | 0 | 22 | 0.33 | 5% | ++ | ++
1571 | New Voltage stabiliser units (SVC), Battery Energy Storage System (BESS) control units in Lithuania, Latvia and Estonia. | 170 | If Studies concerning not known today further infrastructure aspects related to the implementation of the synchronisation of the Baltic States’ system with the continental European network, identify the necessity to install additional SVC. New Battery Energy Storage System (BESS) units - for frequency regulation (FCR and FRR) and to ensure power system secure and stable operation. | 2025 | 1 | Investment on time |  | - | - | AC | None | 0 | 138 | 1.38 | +5%, - 5% | ++ | ++
1118 | Further infrastructure aspects related to the implementation of the synchronisation of the Baltic States’ system with the continental European network | 170 | Further infrastructure aspects ‘not-known-today’ related to the implementation of the synchronisation of the Baltic States’ system with the continental European Network arising from ongoing synchronisation studies | 2025 | 1 | New Investment |  | - | - | AC | None | 0 | 10.5 | 0.105 | +5%, - 5% | ++ | ++
779 | F.Alentejo-Ourique-Tavira | 85 | New double-circuit 400+150 kV OHL F. Alentejo-Ourique-Tavira. The realization of this connection can take advantage of some already existing 150kV single lines, which can be reconstructed as double circuit line 400+150kV. | 2023 | 2 | Ahead of time | ACTransmissionLine | F. Alentejo (by Ourique) | Tavira (by Ourique) | AC | None | 122 | 63 | 0.094 | ±10% | ++ | ++ |  | 11 | RAMSARSite
689 | 689: Vöhringen (DE) - Westtirol (AT) | 47 | Upgrade of an existing over head line to 380 kV, extension of existing and errection of new 380-kV-substations including 380/110-kV-transformers. Transmission route Vöhringen (DE) -Westtirol (AT). This project will increase the current power exchange capacity between the DE, AT. | 2027 | 2 | Delayed | ACTransmissionLine | Vöhringen (DE) | Westtirol (AT) | AC | None | 157 | 174 | 1.3904 | 10% | ++ | ++
1245 | Vigy - Uchtelfangen (or beyond) | 244 | Upgrade of existing transmission OHL between Vigy and Uchtelfangen (or beyond) to increase the thermal cross-border capacity. To reach a higher capacity the options are High Temperature Low Sag (HTLS) conductors or a reconstruction of the tie-line in the existing route . | 2028 | 2 | Delayed | ACTransmissionLine | Vigy (FR) | Uchtelfangen (DE) | AC | None | 65 | 48 | 0.384 | 10% | ++ | ++
1721 | Magadino | 265 | Connection of the Avegno - Gorduno line to the Magadino substation and new 380/220 kV transformer in Magadino | 2035 | 2 | Delayed | ACTransmissionLine | Magadino | Magadino | AC | None | 0 | 34 | 0.17 |  | ++ | ++ |  | 5 3 | Other RAMSARSite None | Emerald Site
1041 | Rem. lim. in Central Italy | 33 | Removing limitations on existing 220 kV grid between Villanova e S.Barbara | 2026 | 2 | Investment on time | ACTransmissionLine | Villanova (IT) | S. Barbara (IT) | AC | None | 350 | 71 | 0.92 |  | ++ | ++ |  | 34 | Other | - | 6 | Other | -
1231 | Muhlbach Eichstetten | 228 | Deployment of a second 400kV circuit at existing double circuit OHL Muhlbach - Eichstetten, instead of the currently operated circuit Eichstetten - Vogelgrun (currently operated with 225kV). Some topological adjustments of the existing grid in the area might prove to be necessary. This also include a transformer in Sierentz substation to balance flows between 225kV and 400kV grid in the area. | 2025 | 2 | Investment on time | ACTransmissionLine | Muhlbach | Eichstetten | AC | None | 32 | 67 | 0.7 | 10% | ++ | ++
1515 | Gramme - Courcelles: HTLS upgrade | 252 | Upgrade of this double-circuit axis to HTLS conductors | 2033 | 2 | Investment on time | ACTransmissionLine | Gramme | Courcelles | AC | None | 60 | 150 | 0.3 | 25% | ++ | ++
1516 | Bruegel - Courcelles: HTLS upgrade | 252 | Upgrade of this double-circuit axis to HTLS conductors | 2035 | 2 | Investment on time | ACTransmissionLine | Bruegel | Courcelles | AC | None | 47 | 110 | 0.2 | 25% | ++ | ++
1517 | Mercator - Bruegel: HTLS upgrade | 252 | Upgrade of this double-circuit axis to HTLS conductors | 2025 | 2 | Investment on time | ACTransmissionLine | Mercator | Bruegel | AC | None | 16 | 80 | 0.1 | 25% | ++ | ++ |  | 1.5 1.5 | HabitatsDirective BirdsDirective |  | 15 | HabitatsDirective
1676 | Mercator - Massenhoven: HTLS upgrade | 252 | Upgrade of this double-circuit axis to HTLS conductors | 2030 | 2 | Investment on time | ACTransmissionLine | Mercator | Massenhoven | AC | None | 36 | 70 | 0.2 | 25 | ++ | ++
1290 | Magadino - Ulrichen | 265 | Replacement and extension of the lines in Western part of canton Tessin. | 2035 | 2 | Investment on time | ACTransmissionLine | Magadino | Ulrichen | AC | None | 1 | 178 | 0.89 | +/- 10% | ++ | ++ |  | 2 1 | Other RAMSARSite None | Emerald Site
1630 | AC Overhead Line Aach-Bofferdange | 328 | New AC Overhead Line between Germany and Luxembourg | 2026 | 2 | Investment on time | ACTransmissionLine | Aach (DE) | Bofferdange (LU) | AC | None | 40 | 83.5 | 0.67 | 10% | ++ | ++ | [7 empty] | The project replaces an existing overhead line.
1518 | Stevin-Izegem/Avelgem: new corridor | 329 | Realisation of a new AC corridor up to 6 GW capacity | 2028 | 2 | Investment on time | ACTransmissionLine | Stevin | Courcelles | AC | None | 90 | 400 | 0.3 | 25% | ++ | ++
1519 | Avelgem-Center: new corridor | 340 | Realisation of a 6 GW new corridor including PSTs | 2028 | 2 | Investment on time | ACTransmissionLine | Avelgem | Center (TBD) | AC | None | 100 | 500 | 0.5 | 25% | ++ | ++
1520 | Sofia West (BG) - Nis 2 (RS) 2nd | 342 | Second interconnection line on the border between Bulgaria and Serbia | 2034 | 2 | Investment on time | ACTransmissionLine | SS Sofia West | SS Nis 2 | AC | None | 123 | 56 | 0.5 | 5% | ++ | ++
1522 | Upgrade of exsisting OHL 220 kV to 400 kV SS Nis 2 - SS Kruševac 1 | 342 | Upgrade of exsisting OHL 220 kV to 400 kV SS Nis 2 - SS Kruševac 1 | 2034 | 2 | Investment on time | ACTransmissionLine | SS Nis 2 | SS Krusevac 1 | AC | None | 72 | 17 | 0.2 | 5% | ++ | ++
1524 | Upgrading of exsisting OHL 220 kV to 400 kV SS Krusevac 1 - SS Kraljevo 3 | 342 | Upgrading of exsisting OHL 220 kV to 400 kV SS Krusevac 1 - SS Kraljevo 3 | 2034 | 2 | Investment on time | ACTransmissionLine | SS Krusevac 1 | SS Kraljevo 3 | AC | None | 48 | 11.5 | 0.1 | 5% | ++ | ++
1533 | New OHL 400 kV Lika – Melina | 343 | New OHL 400 kV Lika – Melina | 2030 | 2 | Investment on time | ACTransmissionLine | Lika (HR) | Melina (HR) | AC | None | 68 | 24.24 | 0.02448 |  | ++ | ++
1534 | New OHL 400 kV Lika – Konjsko | 343 | New OHL 400 kV Lika – Konjsko | 2030 | 2 | Investment on time | ACTransmissionLine | Lika (HR) | Konjsko (HR) | AC | None | 203 | 71 | 0.07308 |  | ++ | ++
1670 | Alqueva-Divor | 85 | New 75 km single-circuit 400 kV OHL Alqueva-Divor. | 2023 | 2 | New Investment | ACTransmissionLine | Alqueva | Divor | AC | None | 75 | 23 | 0.07 | ±10% | ++ | ++
1661 | Construction of new 400kV line Dunowo-Zydowo Kierzkowo | 170 | Dunowo-Zydowo Kierzkowo 400kV line is necessary to assure that after commissioning of Harmony Link and offshore wind farms, full capabilities would be available on the Polish-Lithuanian subsea interconnector. This project includes reconstruction of Dunowo substation with installation of 400/110 kV transformers and construction of new double-circuit 400 kV. | 2025 | 2 | New Investment | ACTransmissionLine | Dunowo | Zydowo Kierzkowo | AC | None | 57.11 | 57.79 | 0.11 | +5%, -5% | ++ | ++
1662 | Construction of new 400kV line Pila Krzewina-Zydowo Kierzkowo | 170 | Pila Krzewina-Zydowo Kierzkowo 400kV line is interrelated with project aiming in building Dunowo-Zydowo Kierzkowo line. This project includes reconstruction and modernization of Pila Krzewina electrical station with installation of 400/110 kV transformers and reactive power compensation devices and construction of new double-circuit 400 kV. | 2025 | 2 | New Investment | ACTransmissionLine | Pila Krzewina | Zydowo Kierzkowo | AC | None | 119 | 110.78 | 0.22 | +5%, -5% | ++ | ++
1663 | Modernization of 400kV OHL Krajnik-Morzyczyn | 170 | To allow effective energy flows in the north-west part of Poland after commissioning of Harmony Link, modernization of “North Line” (line between Krajnik and Gdansk Blonia) is necessary. The first project of North Line is modernization of Krajnik-Morzyczyn 400kV line. | 2023 | 2 | New Investment | ACTransmissionLine | Krajnik | Morzyczyn | AC | None | 41.5 | 2.1 | 0.04 | +5%, -5% | ++ | ++
1664 | Modernization of 400kV OHL Morzyczyn-Dunowo-Slupsk-Zarnowiec | 170 | Modernisation of Morzyczyn-Dunowo-Slupsk-Zarnowiec 400kV line would be the longest part included in modernization of North Line. Because of its length this project consists of three sections: Modernization of Morzyczyn-Dunowo 400 kV, Modernization of Dunowo-Slupsk 400 kV, Modernization of Slupsk-Zarnowiec 400 kV. | 2025 | 2 | New Investment | ACTransmissionLine | Morzyczyn | Zarnowiec | AC | None | 288.5 | 16.6 | 0.3 | +5%, -5% | ++ | ++
1665 | Modernization of 400kV OHL Zarnowiec-Gdansk/Gdansk Przyjazn-Gdansk Blonia | 170 | Modernisation of Zarnowiec-Gdansk/Gdansk Przyjazn-Gdansk Blonia 400kV line would be the last part included in modernization of North Line. | 2024 | 2 | New Investment | ACTransmissionLine | Zarnowiec | Gdansk Blonia | AC | None | 77 | 4.5 | 0.1 | +5%, -5% | ++ | ++
1525 | Uprading exsisting OHL 220 kV to 400 kV SS Kraljevo 3 - SY Pozega | 342 | Uprading exsisting OHL 220 kV to 400 kV SS Kraljevo 3 - SY Pozega | 2034 | 2 | New Investment | ACTransmissionLine | EMS | EMS | AC | None | 70 | 32 | 0.5 | 5% | ++ | ++
1699 | New OHL SS Jagodina 4 - SY Drmno | 342 | New OHL SS Jagodina 4 - SY Drmno | 2034 | 2 | New Investment | ACTransmissionLine | SS Jagodina 4 | SY Drmno | AC | None | 95 | 26 | 0.1 |  | ++ | ++
1700 | OHL SS Pozega - SS Pljevlja | 342 | Upgrading 220 kV OHL SS Pozega - node Vardiste to 2x400 kV and conductoring second circuit on 400 kV OHL SS Bajina Basta - SS Pljevlja from node Vardiste to SS Pljevlja. | 2034 | 2 | New Investment | ACTransmissionLine | SY Pozega | SS Pljevlja | AC | None | 135 | 18 | 0.05 | 5% | ++ | ++
1701 | OHL SS Pozega - SS Visegrad | 342 | Upgrading 220 kV OHL SS Pozega - node Vardiste to 2x400 kV and conductoring second circuit on 400 kV OHL SS Bajina Basta - SS Visegrad from node Vardiste to SS Visegrad.. | 2034 | 2 | New Investment | ACTransmissionLine | SY Pozega | SS Visegrad | AC | None | 65 | 13 | 0.05 | 5% | ++ | ++ |  | 15.7 | OtherNatureProtectionAreasUnderNationalLaw
1639 | Enabling Works 1: Bellacorick-Oldstreet 2 x 245kV OHL | 349 | 2 x 400MW 275kV OHL | 2025 | 2 | New Investment | ACTransmissionLine | Bellacorick Replacement | Oldstreet 400kV | AC | None | 160 | 100 | 0.5 |  | ++ | ++ | [7 empty] | Economic Development Potential in Mayo will be transformed by MAREX Organic Power Interconnector through connecting 1750MW of new RES and providing transmission infrastructure at scale to an undeveloped area allowing for industrial development currently impossible due to lack of transmission infrastructure
1555 | Lienz (AT) - Veneto region (IT) | 375 | Reconstruction of the existing 220kV-interconnection line between Lienz and Veneto Region (IT) | 2027 | 2 | New Investment | ACTransmissionLine | Lienz (AT) | Veneto region (IT) | AC | None | 140 | 175 | 0.9 | 10 | ++ | ++ |  | 31 | Other | - | 3 | Other | -
1697 | Petäjävesi-Hikiä | 1046 | New single circuit 400 kV OHL will be built to the central part of Finland. Enables the integration of renewables and the utilization of full transfer capacity from North to South . | 2030 | 2 | New Investment | ACTransmissionLine | Petäjävesi | Hikiä | AC | None | 175 | 65 | 0.1 | +/-10
2 | Pedralva-Sobrado | 1 | New double circuit Pedralva (PT) - Sobrado (PT) 400kV OHL, (only one circuit installed in a first step). | 2024 | 2 | Rescheduled | ACTransmissionLine | Pedralva (PT) | Sobrado (PT) | AC | None | 67 | 30.4 | 0.066 | ±10% | ++ | ++
463 | Srananagh - South Donegal | 82 | A new EHV overhead line from Srananagh in Co. Sligo to a new substation in south Co. Donegal | 2030 | 2 | Rescheduled | ACTransmissionLine | Srananagh (IE) | New substation in South Donegal (IE) | AC | None | 83 | 171.7 | 0.34 |  | ++ | ++
896 | Omagh South to South Donegal | 82 | A new 275 kV cross border link between a new substation in South Donegal in Ireland and a new substation established south of Omagh in Northern Ireland | 2030 | 2 | Rescheduled | ACTransmissionLine | South Donegal (IE) | Omagh South (NI) | AC | None | 58 | 88.6 | 0.18 |  | ++ | ++
897 | Omagh South to Turleenan | 82 | A new 275 kV overhead line from a new substation established south of Omagh to a new 400/275 kV substation, established at Turleenan by the North South Interconnection Development | 2030 | 2 | Rescheduled | ACTransmissionLine | Omagh South | Turleenan | AC | None | 61 | 135.9 | 0.27 |  | ++ | ++
1212 | New axis Ejea-Aragon region 400 kV | 270 | New AC line (double circuit 400kV) between Ejea and Aragon region where the converter station is located | 2030 | 2 | Rescheduled | ACTransmissionLine | Ejea de los Caballeros | Aragon region | AC | None | 110 | 62.59 | 2.72 | 10% | ++ | ++
1207 | Upgrade Cantegrit-Saucats | 276 | Upgrade of 2* 400 kV lines Cantegrit-Saucats | 2029 | 2 | Rescheduled | ACTransmissionLine | Cantegrit | Saucats | AC | None | 70 | 130 | 2 | 10% | ++ | ++
1208 | Upgrade Cantegrit-Marsillon | 276 | Upgrade of existing 2*225kV line Cantegrit-Marsillon to 1* 400kV | 2029 | 2 | Rescheduled | ACTransmissionLine | Cantegrit | Marsillon | AC | None | 80 | 140 | 2 | 10% | ++ | ++
1532 | New OHL 400 kV Banja Luka - Lika | 343 | New OHL 400 kV Banja Luka - Lika | 2030 | 2 | Rescheduled | ACTransmissionLine | Banja Luka (BA) | Lika (HR) | AC | None | 180 | 53 | 0.0648 |  | ++ | ++
1713 | Lienz (AT) - Obersielach (AT) | 1052 | upgrade from 220 kV to 380 kV | 2030 | 2 | Rescheduled | ACTransmissionLine | Lienz (AT) | Obersielach (AT) | AC | None | 170 | 175 | 1.4 | 10 |  |  |  | 4 | None |  | 81 | None
1715 | Westtirol (AT) - Zell/Ziller (AT) | 1054 | Upgrade of the existing 220kV-line Westtirol - Zell-Ziller and erection of an additional 220/380kV-Transformer. Line length 105km. | 2027 | 2 | Rescheduled | ACTransmissionLine | Westtirol (AT) | Zell-Ziller (AT) | AC | None | 105 | 45 | 1 | 10 |  |  |  | 11 | None |  | 74 | None
1640 | Mares Cable 2: Cross Ireland Interconnector Cable | 349 | 750MW 320kV VSC HVDC Interconnector | 2025 | 2 | New Investment | DCTransmissionLine | Maynooth | Bellacorick Replacement | DC | None | 255 | 186 | 1 | 15% | ++ | ++ | [7 empty] | Economic Development Potential in Mayo will be transformed by MAREX Organic Power Interconnector through connecting 1750MW of new RES and providing transmission infrastructure at scale to an undeveloped area allowing for industrial development currently impossible due to lack of transmission infrastructure
1692 | HVDC from Wilhelmshaven to Uentrop | 1034 | HVDC line from Wilhelmshaven to Uentrop to integrate onshore and offshore wind energy in Northern Germany and transport it to the load centers in Western Germany | 2030 | 2 | New Investment | DCTransmissionLine | Wilhelmshaven | Uentrop | DC | Bipolar | 267 | 1735 | 13.9 | 10
1693 | HVDC from Heide/West to Polsum | 1034 | HVDC line from Heide/West to Polsum to integrate onshore and offshore wind energy in Northern Germany and transport it to the load centers in Western Germany | 2030 | 2 | New Investment | DCTransmissionLine | Heide/West | Polsum | DC | Bipolar | 407 | 2646 | 21.2 | 10
1211 | HVDC Aragon region -Marsillon | 270 | New axis Aragon region -Marsillon | 2030 | 2 | Rescheduled | DCTransmissionLine | Aragon region | Marsillon | DC | None | 230 | 1089.41 | 3.26 | 10% | ++ | ++ |  | 61 | Other |  | 12 | HabitatsDirective
1206 | HVDC Pamplona area - Cantegrit | 276 | HVDC Pamplona area(Spain) -Cantegrit (France) | 2029 | 2 | Rescheduled | DCTransmissionLine | Pamplona area | Cantegrit | DC | None | 225 | 1192 | 5.33 | 10% | ++ | ++ |  | 20 | Other |  | 2 | HabitatsDirective
1638 | Mares Cable 1: Cross Irish Sea Interconnector Cable | 349 | HVDC 750MW 320kV bipole interconnector between UKNG and EIRGRID | 2025 | 2 | Rescheduled | DCTransmissionLine | Bodelwyddan | Maynooth | DC | None | 211 | 253 | 1 | 15% | ++ | ++ | [7 empty] | Economic Development Potential in Mayo will be transformed by MAREX Organic Power Interconnector through connecting 1750MW of new RES and providing transmission infrastructure at scale to an undeveloped area allowing for industrial development currently impossible due to lack of transmission infrastructure
1385 | Greenlink | 286 | A subsea HVDC interconnector between Wales and Ireland | 2023 | 2 | Delayed | OffshoreDCTransmissionCable | Great Island | Pembroke | DC | None | 195 | 396 | 8 | +/-10% | ++ | ++ | + | 0.08 7.8 49.6 0.7 0.4 22.3 36.9 0.7 3.2 | HabitatsDirective HabitatsDirective HabitatsDirective HabitatsDirective HabitatsDirective HabitatsDirective HabitatsDirective OtherNatureProtectionAreasUnderNationalLaw OtherNatureProtectionAreasUnderNationalLaw |  |  |  |  | Greenlink is in the permitting stage. Desk-based environmental and technical assessments have been completed and a programme of environmental surveys has been completed, including a full suite of marine surveys, to ensure the design of the project fully considers all environmental constraints. Routing options have been selected following discussions with statutory consultees and other key stakeholders. The PCI will pass through seven European sites: River Barrow and River Nore SAC (Ireland); Hook Head SAC (Ireland); Pembrokeshire Marine SAC (Wales); Castlemartin Coast SPA (Wales); Limestone Coast of South West Wales SAC (Wales); Skomer, Stokholm and the seas off Pembrokeshire SPA (Wales); and West Wales Marine SAC (Wales). As a result of careful routeing and the adoption of low impact installation technologies (including the adoption of Horizontal direction Drills at landfalls) the PCI has minimised or avoided the most sensitive habitats. The PCI has been unable to avoid crossing reef habitats within the Pembroke Marine Special Area of Conservation. Using the results of subsea surveys and input from technical experts and Natural Resources Wales the PCI has minimised any impact on the reef habitats and appropriate environmental compensation is currently being agreed as part of an ongoing IROPI process lead by Natural Resources Wales. An Environmental Impact Assessment has been completed for the PCI. An Environmental Statement has been completed for the Welsh onshore and marine components of the PCI. An Environmental Impact Assessment Report has been completed for the Irish onshore and marine components. All documents have been submitted apart from the documentation relating to onshore Ireland which is due for submission shortly.
1557 | Italian HVDC tri-terminal link | 339 | Italian HVDC tri-terminal link | 2025 | 2 | Investment on time | OffshoreDCTransmissionCable | SARDINIA REGION | SICILY REGION - SOUTH OF ITALY | DC | None | 900 | 2600 | 13 | 10 | ++ | ++ |  | 43 | Other | - | 36 | Other | -
1521 | New HVDC line between Villanova and Fano existing 400 kV substations | 338 | HVDC lines | 2030 | 2 | New Investment | OffshoreDCTransmissionCable | Villanova | Fano | DC | None | 400 | 1115 | 17.81 | 10 | ++ | ++
1619 | LEG1 | 284 | 2000 MW subsea interconnector associated to a 150 MW solar power plant. | 2025 | 2 | Rescheduled | OffshoreDCTransmissionCable | Tobrouk (Libya) | "Linoperamata (Greece, Crete)" | DC | Bipolar | 370 | 1500 | 30 | 15 | ++ | ++ | [7 empty] | By optimizing the flow between the 2 regions (according to seasonality), LEG1 will bring affordable electrical power to a country which is in great need to develop its industry/commerce to reach stability and peace. Furthermore, LEG1 will offer an export channel to all investors wishing to invest in solar or wind farms (for which Egypt and Libya have great proven potential), creating jobs and hard currency for the respective economies. And more prosperity means less migratory pressure which is of great concern for the EU.
1383 | GridLink | 285 | UK-France, 1.5GW HVDC Interconnector | 2022 | 2 |  | OffshoreDCTransmissionCable | Kingsnorth (UK) | Warande (Gravelines, France) | DC | None | 156 | 906 | 23.9 |  | ++ | ++ | +
1625 | MOG II: connection of up to 2 GW additional offshore wind Belgium | 120 | "MOG II envisions the integration of additional wind farms in the Belgian part of the North Sea. One or more offshore platforms centralize the production from these offshore wind farms, and then transport it via 220 kV subsea AC cables to the onshore substation(s)" | 2028 | 2 | Investment on time | OffshoreSubstation | Offshore (TBD) | Onshore (TBD) | AC | None | 50 | 1100 | 17 | 25% | ++ | 0
1647 | MAREX Wind infeed cable 1 | 349 | 245kV 400MW AC cable | 2025 | 2 | New Investment | OnshoreACTransmissionCable | MAREX Wind 1 | Bellacorick Replacement | AC | None | 25 | 25 | 0.2 | 15% | ++ | ++ | [7 empty] | Economic Development Potential in Mayo will be transformed by MAREX Organic Power Interconnector through connecting 1750MW of new RES and providing transmission infrastructure at scale to an undeveloped area allowing for industrial development currently impossible due to lack of transmission infrastructure
1648 | MAREX Wind Infeed cable 2 | 349 | 245kV 400MW AC cable | 2025 | 2 | New Investment | OnshoreACTransmissionCable | MAREX Wind 2 | Bellacorick Replacement | AC | None | 25 | 25 | 0.2 | 15% | ++ | ++ | [7 empty] | Economic Development Potential in Mayo will be transformed by MAREX Organic Power Interconnector through connecting 1750MW of new RES and providing transmission infrastructure at scale to an undeveloped area allowing for industrial development currently impossible due to lack of transmission infrastructure
1649 | MAREX Wind Infeed cable 3 | 349 | 245kV 400MW AC cable | 2025 | 2 | New Investment | OnshoreACTransmissionCable | Marex Wind 3 | Bellacorick Replacement | AC | None | 25 | 25 | 0.2 | 15% | ++ | ++ | [7 empty] | Economic Development Potential in Mayo will be transformed by MAREX Organic Power Interconnector through connecting 1750MW of new RES and providing transmission infrastructure at scale to an undeveloped area allowing for industrial development currently impossible due to lack of transmission infrastructure
1650 | MAREX Wind Infeed Cable 4 | 349 | 245kV 400MW AC cable | 2025 | 2 | New Investment | OnshoreACTransmissionCable | MAREX Wind 4 | Bellacorick Replacement | AC | None | 20 | 20 | 0.2 | 15% | ++ | ++ | [7 empty] | Economic Development Potential in Mayo will be transformed by MAREX Organic Power Interconnector through connecting 1750MW of new RES and providing transmission infrastructure at scale to an undeveloped area allowing for industrial development currently impossible due to lack of transmission infrastructure
780 | Extension of Ourique substation | 85 | Extension of existing Ourique substation to include 400 kV facilities. | 2023 | 2 | Ahead of time | OnshoreSubstation | Ourique (PT) | - | AC | None | 0 | 4.1 | 0.028 | ±10% | ++ | ++
1620 | Substation Aach | 328 | New 400/220-kV-substation | 2025 | 2 | Investment on time | OnshoreSubstation | N/A | N/A | AC | None | 0 | 40 | 0.32 | 10% | ++ | ++ | [7 empty] | The project replaces an existing overhead line.
1629 | Substation Bofferdange | 328 | New 400/220/110 kV substation including transformer 400/220 kV to be commissioned in Bofferdange (LU) | 2025 | 2 | Investment on time | OnshoreSubstation | N/A | N/A | AC | None | 0 | 42 | 0.34 | 10% | ++ | ++ | [7 empty] | The project replaces an existing overhead line.
1523 | Upgrading SS 220/110 kV Krusevac 1 to 400 kV | 342 | Upgrading SS 220/110 kV Krusevac 1 to 400 kV | 2034 | 2 | Investment on time | OnshoreSubstation | SS Krusevac 1 | SS Krusevac 1 | AC | None | 0 | 6.5 | 0.08 | 5% | ++ | ++
1499 | New 400 kV substation Ladce | 330 | This investment consists of the new 400 kV substation Ladce, which will replace existing 220 kV substation Považská Bystrica and will therefore increase security of supply in this particular region. After commissioning this new 400 kV substation it will be possible to build new 400 kV cross-border OHL from Ladce (SK) to Otrokovice (CZ). | 2027 | 2 | New Investment | OnshoreSubstation | Ladce (SK) | Ladce (SK) | AC | None | 0 | 3.1 | 0.25 | ±10% | ++ | ++
1698 | New 400 kV SY Pozega | 342 | New 400 kV SY Pozega | 2034 | 2 | New Investment | OnshoreSubstation | SS Pozega | SS Pozega | AC | None | 0 | 2 | 0.1 |  | ++ | ++
1641 | Mares Converter Station 3 | 349 | 750MW 320kV VSC HVDC Convertor Station to connect to EIRGRID AC | 2025 | 2 | New Investment | OnshoreSubstation | Bellacorick replacement | Bellacorick replacement | DC | None | 0 | 105 | 3 |  | ++ | ++ | [7 empty] | Economic Development Potential in Mayo will be transformed by MAREX Organic Power Interconnector through connecting 1750MW of new RES and providing transmission infrastructure at scale to an undeveloped area allowing for industrial development currently impossible due to lack of transmission infrastructure
1642 | Mares Converter Station 2 | 349 | 750MW 320kV VSC HVDC Convertor Station to connect to EIRGRID AC | 2025 | 2 | New Investment | OnshoreSubstation | Maynooth | Maynooth | DC | None | 0 | 105 | 3 |  | ++ | ++ | [7 empty] | Economic Development Potential in Mayo will be transformed by MAREX Organic Power Interconnector through connecting 1750MW of new RES and providing transmission infrastructure at scale to an undeveloped area allowing for industrial development currently impossible due to lack of transmission infrastructure
1646 | Mares Converter Station 1 | 349 | 750MW 320kV VSC HVDC Convertor Station to connect to UKNG | 2025 | 2 | New Investment | OnshoreSubstation | Bodelwyddan | Bodelwyddan | DC | None | 0 | 105 | 3 |  | ++ | ++ | [7 empty] | Economic Development Potential in Mayo will be transformed by MAREX Organic Power Interconnector through connecting 1750MW of new RES and providing transmission infrastructure at scale to an undeveloped area allowing for industrial development currently impossible due to lack of transmission infrastructure
1651 | Enabling Works 2: Glinsk Bellacorick Replacement 10 x 245kV bay substation | 349 | 12 bay 245kV substation | 2025 | 2 | New Investment | OnshoreSubstation | Bellacorick Replacement | Bellacorick Replacement | AC | None | 0 | 15 | 0.04 | 15% | ++ | ++ | [7 empty] | Economic Development Potential in Mayo will be transformed by MAREX Organic Power Interconnector through connecting 1750MW of new RES and providing transmission infrastructure at scale to an undeveloped area allowing for industrial development currently impossible due to lack of transmission infrastructure
1652 | Enabling Works 3: 2 x 245kV Connection bays UKNG and associated works | 349 | AC Connection to UKNG system Bodelwyddan 2 number 245kV bays and associated works | 2025 | 2 | New Investment | OnshoreSubstation | Bodelwyddan | Bodelwyddan | AC | None | 0 | 5 | 0.005 | 15% | ++ | ++ | [7 empty] | Economic Development Potential in Mayo will be transformed by MAREX Organic Power Interconnector through connecting 1750MW of new RES and providing transmission infrastructure at scale to an undeveloped area allowing for industrial development currently impossible due to lack of transmission infrastructure
1653 | Enabling Works 4: EIRGRID 2 x 245kV Connection bays at Maynooth and associated works | 349 | EIRGRID 2 x 245kV Connection bays at Maynooth and associated works | 2025 | 2 | New Investment | OnshoreSubstation | Maynooth | Maynooth | AC | None | 0 | 5 | 0.005 | 15% | ++ | ++ | [7 empty] | Economic Development Potential in Mayo will be transformed by MAREX Organic Power Interconnector through connecting 1750MW of new RES and providing transmission infrastructure at scale to an undeveloped area allowing for industrial development currently impossible due to lack of transmission infrastructure
1654 | Enabling Works 5: EIRGRID 2 x 245kV Connection bays at Oldstreet and associated works | 349 | 2 x 245kV Connection bays at Oldstreet and associated works | 2025 | 2 | New Investment | OnshoreSubstation | Oldstreet 220/400kV | Oldstreet 220/400kV | AC | None | 0 | 3 | 0.005 |  | ++ | ++ | [7 empty] | Economic Development Potential in Mayo will be transformed by MAREX Organic Power Interconnector through connecting 1750MW of new RES and providing transmission infrastructure at scale to an undeveloped area allowing for industrial development currently impossible due to lack of transmission infrastructure
1584 | Transformer Gatica | 378 | Only 400 to 220 kV transformer. Not the whole substation | 2025 | 2 | New Investment | OnshoreSubstation | GATICA 400 | GATICA 220 | AC | None | 0 | 8.16 | 0.1224 | 10%
1214 | Ejea de los Caballeros subestation | 270 | New 400kV Ejea de los Caballeros subestation and connection to the lines La Serna-Magallon and Magallon Peñalba | 2030 | 2 | Rescheduled | OnshoreSubstation | Ejea de los Caballeros | Ejea de los Caballeros | AC | None | 0 | 8 | 0.02 | 10% | ++ | ++
1215 | Aragon region subestation | 270 | New 400 kV Aragon region subestation and connection to existing network and future cross border project | 2030 | 2 | Rescheduled | OnshoreSubstation | Aragon region | Aragon region | AC | None | 0 | 10 | 0.03 | 10% | ++ | ++
1210 | New substation Pamplona area | 276 | New substation Pamplona area 400 kV and connection to the 400 kV line Ichaso-Castejón/Muruarte? | 2029 | 2 | Rescheduled | OnshoreSubstation | Pamplona area | Pamplona area | AC | None | 0 | 8 | 0.17 | 10% | ++ | ++
1535 | New Substation 400/110 kV Lika | 343 | New Substation 400/110 kV Lika | 2029 | 2 | Rescheduled | OnshoreSubstation | Lika (HR) | Lika (HR) | AC | None | 0 | 11.9 | 0.1785 |  | ++ | ++
1514 | Power flow control between Vigy and Ensdorf | 244 | Installation of Phase Shift Transformers (PSTs) in Ensdorf substation to allow an optimal use of the capacity increase. | 2027 | 2 | Investment on time | PhaseShiftingTransformer | Vigy (FR) | Ensdorf (DE) | AC | None | 0 | 46 | 0.368 | 10% | ++ | ++
1655 | Enabling Works 6: 2 x 245/400 transformer at EIRGRID 220/400kV Substation Oldstreet | 349 | 2 x 245/400 transformer at EIRGRID 220/400kV Substation Oldstreet | 2025 | 2 | New Investment | PhaseShiftingTransformer | Oldstreet 220/400kV | Oldstreet 220/400kV | AC | None | 0 | 15 | 0.02 | 15 | ++ | ++ | [7 empty] | Economic Development Potential in Mayo will be transformed by MAREX Organic Power Interconnector through connecting 1750MW of new RES and providing transmission infrastructure at scale to an undeveloped area allowing for industrial development currently impossible due to lack of transmission infrastructure
403 | Reinforcements SE2-SE3 in Sweden | 126 | Reactive measures in substations and series compensations in order to increase capacity between SE2 and SE3. Replacement of ageing overhead lines that also will contribute to the increased capacity. The need for capacity is driven by RES integration in northern Sweden and nuclear decommission in southern Sweden. | 2030 | 2 | Investment on time | ReactiveCompensationDevice | Ramsele (SE2) | Hamra (SE3) | AC | None | 1200 | 2800 | 1 | -0.1
1572 | Monitoring and control system upgrades in Lithuania, Latvia and Estonia. Upgrading control systems of exicting HVDC connections (EstLink 1 and EstLink 2 and NordBalt). | 170 | Upgrade of PSS in power stations. AGC impementation and commissioning in SCADA systems and power plants. WAMS and WAMPAC systems. Upgrade of instrument transformers and metering system in transmission network and is necessary to provide stable metering system during synchronous operation with Continental Europe or during island operation in emergency cases. System upgrades (automatics modernisation), SCADA and dispatcher trainer. In order to ensure system stability after high sudden power imbalance during BSPS island operation, activation of fast frequency reserves within view milliseconds via HVDC’s links is crucial. For this project is necessary to perform research, modelling and upgrading control system of HVDC's. | 2025 | 2 | Investment on time |  | - | - | AC | None | 0 | 43.2 | 0.432 | +5%, - 5% | ++ | ++
1702 | Common Baltic Frequency Stability Assessment System (FSAS). Modernisation of System Protection Schemes (SPS) and Under Frequency Load Shedding (UFLS). | 170 | FSAS is a common Baltic IT platform, necessary to ensure frequency monitoring in Baltic system, in order to ensure frequency stability in the region in synchronous mode with the CEN and in izolated mode after incidents. | 2025 | 2 | New Investment |  | - | - | AC | None | 0 | 11.4 | 0.114 | +5%, - 5% | ++ | ++
1703 | Reconstruction of switchgears with shunt reactors | 170 | Due to the synchronisation project the total length of the power lines will increase. Increase in the total length of power lines higher reactive power generation by these lines. In order to reduce the risk that the voltages will rise too high, sufficient amount of reactive power compensation is needed, which can be achieved with the existing shunt reactors. Nevertheless, the shunt reactors need reliable switchgear to help to minimise the risk induced by commutation errors. | 2025 | 2 | New Investment |  |  |  | AC | None | 0 | 4.3 | 0.01 | +5%, - 5% | ++ | ++
4 | V.Minho -R.Pena-Feira | 1 | New double-circuit 400kV OHL Vieira do Minho (PT) - Ribeira de Pena (PT) - Feira (PT). | 2022 | 3 | Ahead of time | ACTransmissionLine | V.Minho (by Ribeira de Pena) | Feira (by Ribeira de Pena) | AC | None | 131 | 69 | 0.155 | ±10% | ++ | ++ |  | 13 7 | Other Other | Habitats Directive Birds Directive Habitats Directive IUCN key biodiversity áreas | 10 | Other | Globally Important Agricultural Heritage Systems (GIAHS)
308 | Vernerov-Vitkov | 200 | New 400 kV double circuit OHL with a transmission capacity of 2x1713 MVA and 83 km length. | 2023 | 3 | Ahead of time | ACTransmissionLine | Vernerov (CZ) | Vitkov (CZ) | AC | None | 83 | 92.96 | 0.06 | -10%, +15% | ++ | ++ | [7 empty] | In accordance with the European and Czech EIA legislation all over-headline projects (investment items 308, 309 and 314) have undergone screening and full scoping EIA assessment and were granted approval opinion by the competent authority, the Ministry of Environment of the Czech Republic. All investment items are included in the Czech Land Use Development Policy which is the land use plan for the entire country adopted on 15th April 2015 by the Czech government under the governmental resolution. The proposed routes (corridor) of the over-headlines were chosen with respect to the municipalities' land plans, transport and technical infrastructures and other development plans of regional importance (local roads, highways, railways, other transport and technical infrastructures). For the purpose of finding a suitable route, a spatial – land oriented technical studies were carried out that evaluated several route variants with consideration of several aspects including environmental ones. The proposed routes were then communicated with relevant and respective local and regional authorities, municipalities and other technical infrastructure owners. The outputs from the above studies were taken as an important input into the environment impact assessment which concluded the projects not to have negative NATURA 2000 sites and were granted an EIA approval.
18 | Beariz (ES) - Fontefria (ES) | 4 | New northern interconnection. New double circuit 400kV OHL between Beariz (ES) - Fontefria (ES). | 2022 | 3 | Delayed | ACTransmissionLine | Beariz (ES) | Fontefria (ES) | AC | None | 30 | 18.69 | 0.49 | 10% | ++ | ++
496 | Fontefria (ES) - Vila Nova de Famalicão (PT) | 4 | New northern interconnection. New 400kV OHL Fontefria (ES) - Ponte de Lima (PT) - Vila Nova de Famalicão (PT). | 2022 | 3 | Delayed | ACTransmissionLine | Fontefria (ES) | Vila Nova de Famalicão (PT) (By Ponte de Lima) | AC | None | 140.21 | 63.92 | 0.208 | 10% | ++ | ++ |  | 0.5 29 3 | HabitatsDirective None HabitatsDirective |  | 1 | HabitatsDirective
313 | Kocin-Mirovka | 35 | Connection of 2 existing 400 kV substations with new double circuit OHL having 120.5 km length and a transmission capacity of 2X1713 MVA. | 2026 | 3 | Delayed | ACTransmissionLine | Kocin (CZ) | Mirovka (CZ) | AC | None | 120.5 | 145.03 | 0.006 | -10%, +15% | ++ | ++ | [7 empty] | In accordance with the European and Czech EIA legislation all over-headline projects (investment items 313 and 315) have undergone screening and full scoping EIA assessment and were granted approval opinion by the competent authority, the Ministry of Environment of the Czech Republic. All investment items are included in the Czech Land Use Development Policy which is the land use plan for the entire country adopted on 15th April 2015 by the Czech government under the governmental resolution. The proposed routes (corridor) of the over-headlines were chosen with respect to the municipalities' land plans, transport and technical infrastructures and other development plans of regional importance (local roads, highways, railways, other transport and technical infrastructures). For the purpose of finding a suitable route, a spatial – land oriented technical studies were carried out that evaluated several route variants with consideration of several aspects including environmental ones. The proposed routes were then communicated with relevant and respective local and regional authorities, municipalities and other technical infrastructure owners. The outputs from the above studies were taken as an important input into the environmental impact assessment which concluded the projects not to have negative NATURA 2000 sites and were granted an EIA approval opinion.
462 | 462 | 81 | A new 138 km single circuit 400 kV 1500 MVA OHL from Turleenan 400/275 kV in Northern Ireland to Woodland 400/220 kV in Ireland. This is a new interconnector project between Ireland and Northern Ireland. | 2023 | 3 | Delayed | ACTransmissionLine | Woodland (IE) | Turleenan (NI) | AC | None | 138 | 363 | 0.6 |  | ++ | ++ |  |  | None |  |  | None
733 | Ekhyddan-Nybro-Hemsjo | 124 | Second phase includes the internal network reinforcements in Sweden to be able to fully utilize the interconnector between Lithuania and Sweden. | 2026 | 3 | Delayed | ACTransmissionLine | Ekhyddan (SE) | Nybro/Hemsjo (SE) | AC | None | 160 | 190 | 0.1 | -0.1 | ++ | ++ |  | 1.6 0.4 | HabitatsDirective OtherNatureProtectionAreasUnderNationalLaw |  | 43 | OtherNatureProtectionAreasUnderNationalLaw
275 | 400 kV OHL Smardan-Gutinas | 138 | Reinforcement of the cross-section between the Western coast of the Black Sea (Dobrogea area) and the rest of the system. New 400kV double circuit OHL (one circuit wired) between existing substations. Line length 140km. | 2024 | 3 | Delayed | ACTransmissionLine | Smardan (RO) | Gutinas (RO) | AC | None | 140 | 53 | 0.26 | -5%, +5% | ++ | ++ |  | 3 | HabitatsDirective |  | 0 | None
1380 | Wurmlach (AT) - Somplago (IT) interconnection | 210 | "Wurmlach (AT) – Somplago (IT) Interconnection is a cross-border electrical line promoted by Alpe Adria Energia Srl. The project concerns a 220kV a.c. merchant line, 300 MW thermal capacity from Somplago substation to new Wurmlach substation, including a Phase Shifter Transformer located in Austria" | 2023 | 3 | Delayed | ACTransmissionLine | SOMPLAGO | WURMLACH | AC | None | 51 | 87.3 | 1.6 | 7% | ++ | 0 |  | 2.2 2.2 | HabitatsDirective BirdsDirective None |  | 0.1 | BirdsDirective
627 | 400kV interconnection RS-BA | 227 | Description of broader context - New double circuit 400kV OHL connecting existing substation Pljevlja (ME) and substation Bajina Basta (RS) and new double circuit 400kV OHL connecting existing substation Visegrad (BA) and substation Bajina Basta (RS). In the first phase one 400 kV circuit would be equiped. In the second phase New SS Bistrica (RS) would be connected to the exisitng double circuit 400 kV OHL between SS Bajina Basta (RS), SS Visegrad (BA) and SS Pljevlja (ME). Part of regional transmission corridor northeast-southwest. | 2026 | 3 | Delayed | ACTransmissionLine | Bajina Basta (RS) | Visegrad (BA) | AC | None | 45.2 | 19.6 | 0.24 | 5% | ++ | ++
628 | 400kV OHL B.Basta-Obrenovac | 227 | Double circuit 400 kV OHL between upgraded substation Bajina Basta and substation Obrenovac. Part of larger regional transmission corridor northeast-southwest. | 2024 | 3 | Delayed | ACTransmissionLine | SS Bajina Basta (RS) | SS Obrenovac (RS) | AC | None | 109 | 55 | 0.66 | 5% | ++ | ++
630 | 400kV interconnection RS-ME | 227 | Description of broader context - New double circuit 400kV OHL (105km RS + 16km ME) connecting existing substation Pljevlja (ME) and substation Bajina Basta (RS) and new double circuit 400kV OHL connecting existing substation Visegrad (BA) and substation Bajina Basta (RS). In the first phase one 400 kV circuit would be equiped. In the second phase New SS Bistrica (RS) would be connected to the exisitng double circuit 400 kV OHL between SS Bajina Basta (RS), SS Visegrad (BA) and SS Pljevlja (ME). Part of regional transmission corridor northeast-southwest. | 2026 | 3 | Delayed | ACTransmissionLine | Bajina Basta (RS) | Pljevlja (ME) | AC | None | 100 | 44.4 | 0.53 | 5% | ++ | ++ |  | 27.8 | OtherNatureProtectionAreasUnderNationalLaw
1384 | Merchant line "Castasegna (CH) - Mese (IT)" | 250 | The planned Transmission project is a merchant line on the swiss-italian border between Castasegna (CH) and Mese (IT). The planned Cable connection in 220 kV AC has a length of around 14 km, 13.5 of witch in Italy. In connection with the realisation of the project a Rationalisation of the 380 and 132 kV Grid in the region Mese (Provincia di Sondrio) is planned. The expected NTC increase is around 200 MW.The main Project elements are (merchant line): 220 kV Connection to the Swiss HVG in Castasegna; 220 kV Cable line of around 14 km between Castasegna and Mese; 220/380 kV Substation with PST 250 MVA in Mese. The Grid Rationalisation in the Region of Mese foresees the following actions: Displacement of 2 km of the 380 kV Line """"Soazza - Bulciago""; ""Realisation of a new 380/132 kV Substation in Mese (Transformation 2 x 250 MVA); Displacement of 0.8 km of 132 kV Lines; Realisation of 2.6 km of 132 kV Cable connections; Demolition of 2.45 km of 380 kV line and 2.3 km of 132 kV lines.""" | 2024 | 3 | Delayed | ACTransmissionLine | Castasegna | Mese | AC | None | 14 | 90 | 0.1 | +/-15 | ++ | 0 | [7 empty] | Environmental positive impact due to the connected grid rationalisation 380/132kV in the region of Mese. Improvement N-1 security for hydro power plant production transmission in Castasegna (CH).
1259 | Beznau - Mettlen | 264 | Optimization of the existing route by voltage conversion to 380 kV, partial reinforcement. | 2029 | 3 | Delayed | ACTransmissionLine | Beznau | Mettlen | AC | None | 64 | 83 | 0.42 | 10% | ++ | ++ |  |  |  |  | 47 | HabitatsDirective
1287 | Bassecourt - Mühleberg | 264 | Reinforcement of the existing route by voltage conversion to 380 kV including a new 380/220 kV transformer in Mühleberg. | 2027 | 3 | Delayed | ACTransmissionLine | Bassecourt | Mühleberg | AC | None | 45.4 | 138 | 0.69 | 10% | ++ | ++
1288 | Mettlen - Ulrichen | 264 | Reinforcement of the existing 220 kV line to 380 kV | 2035 | 3 | Delayed | ACTransmissionLine | Mettlen | Ulrichen | AC | None | 87.1 | 276 | 1.38 | 10% | ++ | ++ |  |  |  |  | 34 | HabitatsDirective
1286 | Chippis - Lavorgo | 266 | Reinforcement by construction of a new 380 kV route including a new 380/220 kV transformer in Mörel | 2029 | 3 | Delayed | ACTransmissionLine | Chippis | Lavorgo | AC | None | 124 | 360 | 1.8 | +/- 10% | ++ | ++
1733 | Bickigen - Chippis | 266 | Bickigen - Chippis: Optimisation of the existing route by voltage conversion to 380 kV | 2027 | 3 | Delayed | ACTransmissionLine | Bickigen | Chippis | AC | None | 106.6 | 50 | 0.25 | + / - 10% | ++ | ++
1473 | Isar/Altheim/Ottenhofen - St. Peter | 313 | New 380kV double circuit OHL Isar/Altheim/Ottenhofen - St. Peter including new 380kV switchgears Altheim, Pirach, Simbach and St. Peter. | 2024 | 3 | Delayed | ACTransmissionLine | Isar/Altheim/Ottenhofen (DE) | St. Peter (AT) | AC | None | 90 | 384 | 3 | 10 | ++ | ++ |  | 4 | OtherNatureProtectionAreasUnderNationalLaw
1476 | Wullenstetten - Border Area (DE-AT) | 322 | Between point Wullenstetten and point border area (DE-AT) an upgrade of an existing 380-kV-line is necessary (grid enhancement). Thereby, a significantly higher transmission capacity is realized. Between switching point Neuravensburg and Austrian National border (AT) a new line with a significantly higher transmission capacity will be constructed in an existing corridor (grid enhancement). | 2025 | 3 | Delayed | ACTransmissionLine | Wullenstetten (DE) | Austrian National border (AT) | AC | None | 95 | 113.5 | 0.9 | 10% | ++ | ++
1478 | Dekani (SI) - Zaule (IT) interconnection | 323 | The Zaule (IT) - Dekani (SI) interconnection is a third party cross-border electrical line promoted by Adria Link Srl, E3 d.o.o. and HSE d.o.o.. The project concerns an underground cable 110kV a.c. merchant line, 150 MW from Zaule (IT) substation to Dekani substation, including a 110/135 kV Phase Shifter Transformer. | 2025 | 3 | Delayed | ACTransmissionLine | DEKANI | ZAULE | AC | None | 11 | 15.6 | 0.3 | 7% | ++ | 0
1482 | Redipuglia (IT) - Vrtojba (SI) Interconnection | 324 | "The Redipuglia (IT) - Vrtojba (SI) interconnection is a third party cross-border electrical line promoted by Adria Link Srl, E3 d.o.o. and HSE d.o.o.. The project concerns an underground cable 110kV a.c. merchant line, 150 MW from Redipuglia (IT) substation to Vrtojba (SI) substation, including a 110/135 kV Phase Shifter Transformer." | 2023 | 3 | Delayed | ACTransmissionLine | REDIPUGLIA | VRTOJBA | AC | None | 22.5 | 24.3 | 0.4 | 7% | ++ | 0
90 | 90 | 33 | Voltage upgrade of the existing 80km Calenzano-Colunga 220kV OHL to 400kV, providing in and out connection to the existing 220/150kV substation of S. Benedetto del Querceto (which already complies with 400kV standards). | 2023 | 3 | Investment on time | ACTransmissionLine | Calenzano (IT) | Colunga (IT) | AC | None | 80 | 188 | 1.36 |  | ++ | ++ |  | 27 | Other | - | 3 | Other
315 | Kocin-Prestice | 35 | Adding second circuit to the existing single circuit OHL with a total transmission capacity of 2x1730 MVA and 117 km length | 2028 | 3 | Investment on time | ACTransmissionLine | Kocin (CZ) | Prestice (CZ) | AC | None | 117 | 175.81 | 0.01 | -10%, +15% | ++ | ++ | [7 empty] | In accordance with the European and Czech EIA legislation all over-headline projects (investment items 313 and 315) have undergone screening and full scoping EIA assessment and were granted approval opinion by the competent authority, the Ministry of Environment of the Czech Republic. All investment items are included in the Czech Land Use Development Policy which is the land use plan for the entire country adopted on 15th April 2015 by the Czech government under the governmental resolution. The proposed routes (corridor) of the over-headlines were chosen with respect to the municipalities' land plans, transport and technical infrastructures and other development plans of regional importance (local roads, highways, railways, other transport and technical infrastructures). For the purpose of finding a suitable route, a spatial – land oriented technical studies were carried out that evaluated several route variants with consideration of several aspects including environmental ones. The proposed routes were then communicated with relevant and respective local and regional authorities, municipalities and other technical infrastructure owners. The outputs from the above studies were taken as an important input into the environmental impact assessment which concluded the projects not to have negative NATURA 2000 sites and were granted an EIA approval opinion.
458 | HINP-SEAB New Double Circuit | 78 | New 400kV substation at Hinkley Point. New 400kV transmission route from Hinkley Point to Seabank. Reconstruction of Bridgewater substation for 400kV operation. Uprate Bridgewater - Melksham to 400kV. | 2024 | 3 | Investment on time | ACTransmissionLine | Hinkley Point (GB) | Seabank (GB) | AC | None | 60 | 1104 | 16.2 |  | ++ | ++
396 | 3rd AC Finland-Sweden north | 111 | Third AC 400 kV overhead line interconnector between Finland north and Sweden SE1. | 2025 | 3 | Investment on time | ACTransmissionLine | Keminmaa (Finland) | Messaure (Sweden, bidding area SE1) | AC | None | 200 | 238 | 0.11 | -0.1 | ++ | ++
1710 | Keminmaa-Pyhänselkä | 111 | The investment is a 400 kV overhead line in North Finland. It is part of the 3rd AC cross border project between Finland and Sweden and will enable its full capacity to be utilized. The project will also allow integration of new RES generation at Bothnian bay. | 2024 | 3 | Investment on time | ACTransmissionLine | Keminmaa | Pyhänselkä | AC | None | 156 | 59 | 0.19 | -0.1 | ++ | ++
86 | 86 | 127 | New 178km double circuit 400kV OHL between existing Foggia and Villanova 400kV substations, also connected in and out to the Larino and Gissi substations. | 2024 | 3 | Investment on time | ACTransmissionLine | Foggia (IT) | Villanova (IT) | AC | None | 178 | 397 | 3.17 |  | ++ | ++ |  | 8 | Other | - | 0 | None
256 | 256 | 142 | New interconnection line BG-GR by a 151km single circuit 400kV OHL. | 2023 | 3 | Investment on time | ACTransmissionLine | Maritsa East 1 (BG) | N.Santa (GR) | AC | None | 151 | 80 | 1.1 | +10%, -10% | ++ | ++ |  | 0.1 4.4 | HabitatsDirective BirdsDirective
270 | Upgrade of the existing 220kV double circuit OHL Resita -Timisoara - Sacalaz - Arad to 400kV double circuit line | 144 | Upgrade of an existing 220 kV AC double circuit line (OHL) between Resita - Timisoara (RO) to 400 kV double circuit line Resita-Timisoara/Sacalaz of which: 74 km from Resita to Timisoara and 92 km from Resita to Sacalaz , both overhead lines will be built on common towers up to Icloda on 58 km. Upgrade of the existing 220 kV AC double circuit line (OHL) Timisoara/Sacalaz-Arad to 400 kV on 67 km of which: 14 km of line will be build single circuit between Sacalaz-C.Aradului-""connection point"", 11 km single circuit from Timisoara to ""connection point"" and the rest 42 km of the line will be double circuit from ""connection point"" to Arad. | 2025 | 3 | Investment on time | ACTransmissionLine | Resita (RO) | Timisoara-Sacalaz-Arad (RO) | AC | None | 274 | 75 | 0.5 | -5%, +5% | ++ | ++ |  | 34.5 | HabitatsDirective |  | 0 | None
382 | New 330 kV OHL Vilnius-Neris | 170 | New 330 kV OHL Vilnius-Neris | 2025 | 3 | Investment on time | ACTransmissionLine | Vilnius | Neris | AC | None | 80 | 23.7 | 0.024 | +5%, - 5% | ++ | ++
1010 | 330 kV OHL Tartu-Valmiera | 170 | Reinforcement of existing 330 kV OHL. The investment is also a backbone for Baltics Synchronization with CESA. | 2025 | 3 | Investment on time | ACTransmissionLine | Tartu | Valmiera | AC | None | 133 | 30.66 | 0.094 | +5%, - 5% | ++ | ++
1011 | Valmiera -Tsirguliina 330 kV | 170 | Reinforcement of existing 330 kV OHL. The investment is also a backbone for Baltics Synchronization with CESA | 2025 | 3 | Investment on time | ACTransmissionLine | Tsirguliina | Valmiera | AC | None | 60 | 22 | 0.13 | +5%, - 5% | ++ | ++
1012 | 330 kV OHL Tartu-Balti (L300) | 170 | Reinforcement of existing 330 kV OHL between Balti and Tartu 330 kV substations in Estonia. Old line will be replaced with new towers and wires of 3x400 mm2 in phase. The thermal capacity of the line is planned 1143 MVA. The investment is also a backbone for Baltics Synchronization with CESA (project nr 170). | 2023 | 3 | Investment on time | ACTransmissionLine | Balti | Tartu | AC | None | 168 | 51.2 | 0.11 | +5%, - 5% | ++ | ++
1013 | Viru-Tsirguliina 330kV OHL | 170 | Reinforcement of existing 330 kV OHL between Viru and Tsirguliina 330 kV substations in Estonia. Old line will be replaced with new towers and wires of 3x400 mm2 in phase. The thermal capacity of the line is planned 1143 MVA. The investment is also a backbone for Baltics Synchronization with CESA (project nr 170). | 2025 | 3 | Investment on time | ACTransmissionLine | Viru | Tsirguliina | AC | None | 243 | 73.2 | 0.17 | +5%, - 5% | ++ | ++
1634 | New 330 kV OHL Bitenai - KHAE | 170 | New 330 kV OHL Bitenai-KHAE. One part of the new line will be constructed as second circuit on exicting 330 kV OHL Bitenai-Jurbarkas (44km), one part will be new line (74 km), and as third part of new line will be used part of exicting 330 kV OHL KHAE-Sovetsk. | 2025 | 3 | Investment on time | ACTransmissionLine | Bitenai | KHAE | AC | None | 234 | 42.1 | 0.042 | +5%, - 5% | ++ | ++
1659 | New 330 kV OHL Darbenai-Bitenai | 170 | New 330 kV OHL Darbenai-Bitenai | 2025 | 3 | Investment on time | ACTransmissionLine | Darbenai | Bitenai | AC | None | 147 | 62.8 | 0.063 | +5%, -5% | ++ | ++ |  | 10.38 | OtherNatureProtectionAreasUnderNationalLaw
1018 | DKW-DE, Westcoast, TYNDP ID 183.1018 | 183 | New 380 kV line DKW-DE between Klixbuell (DE) and Endrup (DKW) as part of connection Endrup-Brunsbüttel | 2023 | 3 | Investment on time | ACTransmissionLine | Klixbüll (DE) | Endrup (DKW) | AC | None | 92 | 210 | 2 |  | ++ | ++ |  | 5 | OtherNatureProtectionAreasUnderNationalLaw
997 | 997 Pleinting - St. Peter | 187 | new 380-kV-line Pleinting (DE) - St. Peter (AT) on exting OHL corridor | 2028 | 3 | Investment on time | ACTransmissionLine | Pleinting (DE) | St. Peter (AT) | AC | None | 60 | 197 | 1.576 | 10 | ++ | ++ |  |  |  |  | 2 | OtherNatureProtectionAreasUnderNationalLaw
353 | Krajnik-Baczyna | 230 | Construction of new 400 kV double circuit line Krajnik - Baczyna. One circuit will be operating temporarily on 220 kV between stations Krajnik and Gorzów with winter thermal limit 1290 A, summer thermal limit 990 A. | 2021 | 3 | Investment on time | ACTransmissionLine | Krajnik (PL) | Baczyna (PL) | AC | None | 70 | 45.2 | 0.116 | 5% | ++ | ++ |  | 1 | BirdsDirective
1456 | Massenhoven - Van Eyck: HTLS upgrade | 252 | Installation of a second circuit (in HTLS) and upgrade of existing circuit to HTLS | 2024 | 3 | Investment on time | ACTransmissionLine | Massenhoven (BE) | Van Eyck (BE) | AC | None | 90 | 120 | 0.4 | 25% | ++ | ++ |  | 23 23 | HabitatsDirective BirdsDirective |  | 32 | HabitatsDirective
604 | BRABO III: Liefkenshoek - Mercator | 297 | The existing 150kV overhead will be upgraded to a single 380kV overhead line between the site Liefkenshoek and the substation Mercator. To facilitate this upgrade, the adjacent 150kV grid will be adapted. | 2025 | 3 | Investment on time | ACTransmissionLine | Liefkenshoek (BE) | Mercator (BE) | AC | None | 19 | 70 | 0.1 | 25% | ++ | ++ |  | 4 | BirdsDirective |  | 14.7 | HabitatsDirective
1688 | Nuojuankangas-Huutokoski | 1046 | New single circuit 400 kV OHLs will be built from central part of Finland to the northern area to increase the capacity between North and South Finland. Enables integration of renewables to the northern part of the country. | 2028 | 3 | New Investment | ACTransmissionLine | Nuojuankangas | Huutokoski | AC | None | 290 | 120 | 0.1 | +/- 10
1689 | Tuomela B-Nuojuankangas | 1046 | New single circuit 400 kV OHL will be built to the northern part of Finland. Enables the integration of renewables to the northern part of the country and the increasing power transfer from North to South . | 2029 | 3 | New Investment | ACTransmissionLine | Tuomela B | Nuojuankangas | AC | None | 100 | 70 | 0.1 | +/- 10
1727 | Montecorvino-Avellino and Nord-Ben. in Campania | 1059 | New 400 kV between Montecorvino-Avellino and Nord-Ben. in Campania | 2030 | 3 | New Investment | ACTransmissionLine | Montecorvino (IT) | Benevento (IT) | AC | None | 0 | 212 | 1.97
1490 | Ens-Zwolle | 103 | Upgrade of existing 380kV circuits between Ens and Zwolle from 2* 2,5 kA to 2* 4kA circuits by replacing the conductors with HTLS conductors | 2024 | 3 | Rescheduled | ACTransmissionLine | Ens | Zwolle | AC | None | 32 | 41 | 0.4 | +/- 10% | ++ | ++
1539 | Krimpen-Geertruidenberg | 103 | Upgrade of existing 380kV circuits between Krimpen and Geertruidenberg from 2* 2,5 kA to 2* 4kA circuits by replacing the conductors with HTLS conductors | 2023 | 3 | Rescheduled | ACTransmissionLine | Krimpen | Geertruidenberg | AC | None | 35 | 41 | 0.4 | +/- 10% | ++ | ++
1540 | Eindhoven-Maasbracht | 103 | Upgrade of existing 380kV circuits between Eindhoven and Maasbracht from 2* 2,5 kA to 2* 4kA circuits by replacing the conductors with HTLS conductors | 2025 | 3 | Rescheduled | ACTransmissionLine | Eindhoven | Maasbracht | AC | None | 50 | 50 | 0.5 | +/- 10% | ++ | ++
257 | 257 | 142 | New 94km single circuit 400kV OHL in parallel to the existing one. | 2022 | 3 | Rescheduled | ACTransmissionLine | Maritsa East 1 (BG) | Plovdiv (BG) | AC | None | 94 | 57 | 0.7 | +10%, -10% | ++ | ++
355 | Mikulowa - Swiebodzice | 230 | Construction of new 400 kV double circuit line Mikulowa-Swiebodzice in place of existing 220 kV line. One circuit will be operating temporarily on 220 kV between stations Mikulowa and Swiebodzice with winter thermal limit 1290 A, summer thermal limit 990 A. | 2024 | 3 | Rescheduled | ACTransmissionLine | Mikulowa (PL) | Swiebodzice (PL) | AC | None | 100 | 89 | 0.307 | 5% | ++ | ++
1232 | Baczyna-Plewiska | 230 | Construction of new 400 kV double circuit line Baczyna - Plewiska | 2022 | 3 | Rescheduled | ACTransmissionLine | Baczyna | Plewiska | AC | None | 147 | 91.9 | 0.7 | 5% | ++ | ++
1544 | ZuidWest3808 Oost | 346 | New 380 kV substation Tilburg; New 380 kV double circuit line 2645MVA between Rilland and Tilburg | 2029 | 3 | Rescheduled | ACTransmissionLine | Rilland | Tilburg | AC | None | 80 | 1090 | 5.5 | 10% | ++ | ++ | +
645 | ITA-3 | 1059 | New 400kV OHL between the existing substations of Laino and Altomonte in Calabria (investment previously included in P127). | 2027 | 3 | Rescheduled | ACTransmissionLine | Laino (IT) | Altomonte (IT) | AC | None | 50 | 186 | 2.41
616 | Salgareda - Bericevo | 150 | New HVDC link between Salgareda (IT) and Bericevo/Divaca (SI) | 2028 | 3 | Delayed | DCTransmissionLine | Salgareda (IT) | Bericevo (SI) | DC | None | 0 | 755 | 4 | 15 | ++ | ++ |  | 169 2 | OtherNatureProtectionAreasUnderNationalLaw Other | - | 174 2 | OtherNatureProtectionAreasUnderNationalLaw Other | -
1014 | Greenconnector | 174 | Greenconnector is an HVDC interconnector project between Italy and Switzerland for power transport using DC cables rather than overhead lines. The route length is about 165 km. The design power is 1000 MW (1200 MW in overload condition), while the DC voltage is +/- 400 kV DC. Two cables will be installed, working with a bipolar scheme. Great part of the cables route will exploit a section of an existing oil pipeline, no longer in service since January 1997. This pipeline crosses the Italian and Switzerland border at Splgenpass and is running close by the two end stations of the Greenconnector project (Bonaduz in Graubunden Canton and Verderio Inferiore, Lecco). The cables will be pulled inside the pipeline itself, reducing the amount of civil works required before and after cable laying and therefore limiting even temporary environmental impact. For about 47 km the cables will run across the Como lake. | 2024 | 3 | Delayed | DCTransmissionLine | Verderio | Bonaduz | DC | Bipolar | 165 | 660 | 2 | -66.6667 | ++ | ++ | [7 empty] | The project avoids the dismatling of about 80 km of an existing oil pipeline no longer in use. The pipeline crosses very sensitive environmental areas (Protected and mountain areas). Should the pipeline be dismissed, the estimated costs add up to about 25 million euros (supporting documents are available upon request). So our project generates a positive residual impact equal to such amount.
664 | HVDC Line C | 235 | New DC-lines to integrate new wind generation from Northern Germany towards Southern Germany and Southern Europe for consumption and storage. | 2026 | 3 | Delayed | DCTransmissionLine | Brunsbüttel, Wilster | Großgartach, Grafenrheinfeld | DC | None | 700 | 9560 | 76.5 | -0.2 | ++ | ++ |  | 121 | OtherNatureProtectionAreasUnderNationalLaw |  | 157 | OtherNatureProtectionAreasUnderNationalLaw
635 | Elmed Project | 29 | New interconnection between Italy and Tunisia - new HVDC submarine cable | 2027 | 3 | Investment on time | DCTransmissionLine | Sicily Area (IT) | Tunisia node | DC | Monopolar | 200 | 600 | 3 |  | ++ | ++ |  | 9 | Other | - | 0 | None
665 | Wolmirstedt-Isar | 130 | New DC-line to integrate new wind generation from control area 50Hertz especially Mecklenburg-Vorpommern, Brandenburg and Sachsen-Anhalt towards Central/south Europe for consumption and storage. | 2025 | 3 | Investment on time | DCTransmissionLine | Wolmirstedt (DE) | Isar (DE) | DC | None | 540 | 4220 | 33.8 | -0.15 | ++ | ++ |  | 78 | OtherNatureProtectionAreasUnderNationalLaw |  | 45 | OtherNatureProtectionAreasUnderNationalLaw
661 | HVDC Line A-North | 132 | New HVDC line from Emden to Osterath to integrate new wind generation especially from North Sea towards Central Germany for consumption. | 2025 | 3 | Investment on time | DCTransmissionLine | Emden East (DE) | Osterath (DE) | DC | Bipolar | 300 | 2300 | 18.4 | 10% | ++ | ++ |  | 3.5 16.1 11.0 3.9 2.6 | HabitatsDirective BirdsDirective RAMSARSite IUCNKeyBiodiversityAreas OtherNatureProtectionAreasUnderNationalLaw |  | 28.6 8 | HabitatsDirective MarinStrategyFrameworkDirective
1458 | SACOI3 | 299 | New HVDC triterminal link between Italy mainland, Corsica and Sardinia replacing existing link SACOI2 | 2024 | 3 | Investment on time | DCTransmissionLine | Codrongianos - Lucciana | Suvereto | DC | Bipolar | 300 | 900 | 7 | 10 | ++ | ++ |  | 1 | Other | - | 3 | Other | -
1717 | Interconnection between Crete and Attica (Phase II) | 1055 | New symmetric bipolar submarine HVDC-VSC link between Crete and Attica | 2022 | 3 | New Investment | DCTransmissionLine | Damasta | Koumoundouros | DC | Bipolar | 373 | 1020 | 1.5 | 9 |  |  |  | 5.2 4.48 | HabitatsDirective OtherNatureProtectionAreasUnderNationalLaw |  | 14.9 | HabitatsDirective
660 | HVDC Line A South - Ultranet | 254 | New HVDC-lines from Osterath to Philippsburg to integrate new wind generation especially from North Sea towards Central-South Germany for consumption and storage. | 2024 | 3 | Rescheduled | DCTransmissionLine | Osterath (DE) | Philippsburg (DE) | DC | Bipolar | 340 | 1250 | 10 | 10% | ++ | ++ |  | 12.6 16.7 209 | HabitatsDirective BirdsDirective OtherNatureProtectionAreasUnderNationalLaw |  | 4.5 15.4 183.3 49.5 | HabitatsDirective RAMSARSite IUCNKeyBiodiversityAreas MarinStrategyFrameworkDirective
987 | France-Alderney-Britain | 153 | France-Alderney-Britain (FAB) is a new 220km-long HVDC subsea interconnection between Exeter (UK) and Menuel (France) with VSC converter station at both ends. Expected rated capacity is 2*700 MW. | 2025 | 3 | Delayed | OffshoreDCTransmissionCable | Menuel (FR) | Exeter (GB) | DC | None | 220 | 870 | 7.6 | +/- 27% | ++ | ++ | + | 10 | HabitatsDirective |  | 0 | None
1382 | NorthConnect | 190 | A 665 km long subsea interconnector between Norway and Scotland is planned to be realized in 2024. The main driver for the project is to integrate the hydro-based Norwegian system with the thermal/nuclear/wind-based British system. The interconnector will improve security of supply both in Norway in dry years and in Great Britain in periods with negative power balance (low wind, low solar, high demand etc.). Additionally the interconnector will be positive both for the European market integration, for facilitating renewable energy and also for preparing for a power system with lower CO2-emissions. The interconnector is planned to be a 500 kV 1400 MW HVDC subsea interconnector between western Norway and eastern Scotland. | 2024 | 3 | Delayed | OffshoreDCTransmissionCable | Sima | Peterhead | DC | Monopolar | 665 | 1675 | 10 | Costs are based on feedback from the supply chain; CAPEX same as previous input to ENTSO-E, and OPEX adjusted from 30 to 10. | ++ | ++ | +
1381 | AQUIND Interconnector | 247 | AQUIND Interconnector is a proposed High Voltage Direct Current (HVDC) subsea and underground electric power transmission link between Great Britain (Lovedean substation, Hampshire) and France (Barnabos substation, Seine-Maritime) with a net transmission capacity of 2,000 MW. The Interconnector is designed as two parallel monopole 1000 MW circuits employing Voltage Source Converter technology. | 2023 | 3 | Delayed | OffshoreDCTransmissionCable | Lovedean (GB) | Barnabos (FR) | DC | Monopolar | 240 | 1400 | 14 | +/-10 | ++ | ++ | +
38 | HVDC Gatica-Cubnezais | 16 | New HVDC interconnection in the western part of the border via DC subsea cable in the Biscay Gulf (cable and converters at the end). | 2027 | 3 | Investment on time | OffshoreDCTransmissionCable | Gatica (ES) | Cubnezais (FR) | DC | None | 370 | 1750 | 10.2 | 2022-04-11 | ++ | ++ |  | 11 | Other |  | 0.269 | HabitatsDirective
810 | France Ireland Interconnector | 107 | A new HVDC subsea connection between Ireland and France | 2026 | 3 | Investment on time | OffshoreDCTransmissionCable | Knockraha (IE) | La Martyre (FR) | DC | None | 500 | 930 | 8.4 | +/- 10% | ++ | ++ | + | 33.277 | Other | offshore and onshore sensitivity | 10.072 | Other | offshore and onshore sensitivity
1034 | New HVDC interconnector "Harmony Link" | 170 | New HVDC subsea cable connection between Lithuania and Poland. The project includes HVDC submarine and land cable system and converter stations at each end | 2026 | 3 | Investment on time | OffshoreDCTransmissionCable | Darbenai | Zarnowiec | DC | Bipolar | 400 | 682.6 | 2.45 | +5%, - 5% | ++ | ++
995 | Hansa PowerBridge I | 176 | New HVDC interconnector between Sweden (SE4) and Germany (50 Hertz) aiming to enhance the integration of the Nordic and the continental power market. Moreover the interconnector facilitates RES integration and increases the system adequacy in both systems. | 2026 | 3 | Investment on time | OffshoreDCTransmissionCable | Hurva (SE4) | Guestrow (DE) | DC | None | 300 | 660 | 1 | -0.1 | ++ | ++ | + | 20 8 | HabitatsDirective OtherNatureProtectionAreasUnderNationalLaw |  |  |  |  | Tourist area with protected biotopes, water protection areas: 4 km
1628 | NeuConnect Interconnector | 309 | 1.4GW HVDC Interconnector between UK and Germany | 2023/4 | 3 | New Investment | OffshoreDCTransmissionCable | Grain West 400kV Substation | Fedderwarden 380kV Substation | DC | None | 700 | 1600 | 32.5 |  | ++ | ++ | +
1407 | EuroAsia Interconnector | 219 | The Euro Asia Interconnector consists of a 500 kV DC underwater electric cable and any essential equipment and/or installation for interconnecting the Cypriot, Israeli and the Greek transmission networks (offshore). The Interconnector will have a capacity of 2000 MW and a total length of around 820 nautical miles/around 1200 km (approx. 329 km between CY and IL, 879 km between CY and Crete) and allow for reverse transmission of electricity. | 2023 | 3 | Rescheduled | OffshoreDCTransmissionCable | Hadera Site | Kofinou Site | DC | Bipolar | 310 | 1922 | 17.8 |  | ++ | ++
1409 | EuroAsia Interconnector | 219 | The Euro Asia Interconnector consists of a 500 kV DC underwater electric cable and any essential equipment and/or installation for interconnecting the Cypriot, Israeli and the Greek transmission networks (offshore). The Interconnector will have a capacity of 2000 MW and a total length of around 820 nautical miles/around 1200 km (approx. 329 km between CY and IL, 879 km between CY and Crete) and allow for reverse transmission of electricity. | 2023 | 3 | Rescheduled | OffshoreDCTransmissionCable | Kofinou Site | Korakia (Crete)Site | DC | Bipolar | 898 | 1922 | 17.8 |  | ++ | ++
474 | Substation Ribeira de Pena | 1 | New 400/60kV substation in Ribeira de Pena. | 2021 | 3 | Ahead of time | OnshoreSubstation | Ribeira de Pena (PT) | - | AC | None | 0 | 7.4 | 0.054 | ±10% | ++ | ++
499 | Beariz 400kV (ES) | 4 | New northern interconnection. New 400kV substation Beariz (ES), previously Boboras | 2022 | 3 | Delayed | OnshoreSubstation | Beariz (ES) | Beariz (ES) | AC | None | 0 | 7.17 | 0.17 | 10% | ++ | ++
500 | Ponte de Lima (PT) | 4 | New 400/150kV substation Ponte de Lima (PT), previously V. Castelo. | 2022 | 3 | Delayed | OnshoreSubstation | Ponte de Lima (PT) | Ponte de Lima (PT) | AC | None | 0 | 10.5 | 0.054 | 10% | ++ | ++
705 | 400 kV Substation Timisoara | 144 | Replacement of 220 kV substation Timisoara with 400 kV substation (2x250 MVA 400/110 kV) | 2025 | 3 | Delayed | OnshoreSubstation | Timisoara (RO) | Timisoara (RO) | AC | None | 0 | 18 | 0.18 | -5%, +5% | ++ | ++ |  | 0 | None |  | 0 | None
631 | 400kV SS B.Basta upgrade | 227 | Upgrade of existing 220/110 kV substation in Bajina Basta to 400/220/110 kV substation as part of overall western Serbia system upgrade to 400 kV voltage level. Part of larger regional transmission corridor northeast-southwest. | 2024 | 3 | Delayed | OnshoreSubstation | Bajina Basta (RS) | Bajina Basta (RS) | AC | None | 0 | 11 | 0.13 | 5% | ++ | ++
1035 | Baczyna | 230 | Construction of new 400/110 kV Substation Baczyna to connect the new line Krajnik-Baczyna. | 2021 | 3 | Investment on time | OnshoreSubstation | Baczyna | n.a. | AC | None | 0 | 24.9 | 0.675 | 5% | ++ | ++
498 | SE Fontefria 400/220kV | 4 | New northern interconnection. New 400kV substation Fontefria (ES), previously O Covelo. | 2022 | 3 | Delayed | Transformer | Fontefria (ES) | REE | AC | None | 0 | 13.16 | 0.17 | 10% | ++ | ++
1632 | New 330 kV Musa substation | 170 | New 330 kV Musa substation | 2025 | 3 | Investment on time |  | Musa | - | AC | None | 0 | 6.14 | 0.006 | +5%, - 5% | ++ | ++
1660 | New 330 kV Darbenai substation | 170 | New 330 kV Darbenai substation, necessary for the connection of the new 330 kV lines as well as new HVDC subsea cable known as Harmony Link. This project includes territory planning, land acquisition and construction phases. | 2025 | 3 | Investment on time |  | Darbenai | - | AC | None | 0 | 12 | 0.012 | +5%, - 5% | ++ | ++
1669 | Synchronous condensers in Lithuania, Latvia and Estonia | 170 | Synchronous condensers providing inertia, voltage stability,frequency stability and short-circuit power in Lithuania, Latvia and Estonia | 2025 | 3 | Investment on time |  | 330 kV substations in the Baltics | - | AC | None | 0 | 333 | 4.5 | +5%, - 5% | ++ | ++
309 | Vitkov-Prestice | 200 | New 400 kV double circuit OHL with transmission capacity of 2x1713 MVA and 87 km length. | 2021 | 4 | Ahead of time | ACTransmissionLine | Vitkov (CZ) | Prestice (CZ) | AC | None | 87 | 109.73 | 0.005 | -10%, +15% | ++ | ++ | [7 empty] | In accordance with the European and Czech EIA legislation all over-headline projects (investment items 308, 309 and 314) have undergone screening and full scoping EIA assessment and were granted approval opinion by the competent authority, the Ministry of Environment of the Czech Republic. All investment items are included in the Czech Land Use Development Policy which is the land use plan for the entire country adopted on 15th April 2015 by the Czech government under the governmental resolution. The proposed routes (corridor) of the over-headlines were chosen with respect to the municipalities' land plans, transport and technical infrastructures and other development plans of regional importance (local roads, highways, railways, other transport and technical infrastructures). For the purpose of finding a suitable route, a spatial – land oriented technical studies were carried out that evaluated several route variants with consideration of several aspects including environmental ones. The proposed routes were then communicated with relevant and respective local and regional authorities, municipalities and other technical infrastructure owners. The outputs from the above studies were taken as an important input into the environment impact assessment which concluded the projects not to have negative NATURA 2000 sites and were granted an EIA approval.
273 | 400kV OHL Cernavoda-Stalpu | 138 | Reinforcement of the cross-section between the Western coast of the Black Sea (Eastern Romania) and the rest of the system. A new 400 kV AC OHL double circuit of 159 km shall be built between the 400 kV substation Cernavoda and the existing 220/110 kV Stalpu substation, which shall be replaced with a 400/110 kV substation (onshore). One of the two circuits shall be connected in-out to the 400 kV substation Gura Ialomitei, situated in the vicinity of the new line. | 2023 | 4 | Delayed | ACTransmissionLine | Cernavoda (RO) | Stalpu (RO) | AC | None | 159 | 65 | 0.36 | -5%, +5% | ++ | ++ |  | 1 | HabitatsDirective |  | 0 | None
238 | New_400 kV OHL RO-RS | 144 | New 131 km double circuit 400kV OHL between Romania and Serbia (63 km on Romanian (thermal limit 2513 A) side and 68 km on Serbian (thermal limit 1920 A) side). | 2024 | 4 | Delayed | ACTransmissionLine | Resita (RO) | Pancevo (RS) | AC | None | 131 | 47 | 0.23 | -5%, +5% | ++ | ++ |  | 1 | HabitatsDirective |  | 0 | None
269 | 400 kV OHL Portile de Fier-Resita | 144 | New 116 km 400kV OHL single circuit between existing substation 400 kV Portile de Fier and new 400 kV substation Resita. | 2024 | 4 | Delayed | ACTransmissionLine | Portile de Fier (RO) | Resita (RO) | AC | None | 116 | 25 | 0.13 | -5%, +5% | ++ | ++ |  | 30 | HabitatsDirective |  | 0 | None
939 | Conneforde - Emden | 207 | New 380-kV-line in existing OHL corridor for integration of RES | 2023 | 4 | Delayed | ACTransmissionLine | Conneforde | Emden/Ost | AC | None | 60 | 220 | 1.8 | -0.1 | ++ | ++
151 | Ganderkesee - Wehrendorf | 208 | New line (length ca. 95km), extension of existing and erection of substations, erection of 380/110kV-transformers. | 2023 | 4 | Delayed | ACTransmissionLine | Wehrendorf (DE) | Ganderkesee (DE) | AC | None | 95 | 330 | 2.6 | -0.1 | ++ | ++
156 | Niederrhein-Dörpen | 208 | New 380 kV double circuit overhead line Dörpen - Niederrhein including extension of existing substations. | 2023 | 4 | Delayed | ACTransmissionLine | Niederrhein (DE) | Dörpen/West (DE) | AC | None | 182 | 540 | 4.3 | -0.1 | ++ | ++
1526 | 400 kV OHL Lastva - Pljevlja | 227 | 400 kV OHL Lastva - Pljevlja | 2019 | 4 | Delayed | ACTransmissionLine | SS Lastva | SS Pljevlja | AC | None | 151 | 67.5 | 1.35 | 5% | ++ | ++
1284 | Pradella - La Punt | 264 | Reinforcement of the existing route | 2022 | 4 | Delayed | ACTransmissionLine | Pradella | La Punt | AC | None | 49 | 102 | 0.51 | 10% | ++ | ++ |  | 3 | Other None | Emerald Site
1734 | Chamoson - Chippis | 266 | Chamoson - Chippis: Reinforcement by new construction of a 380 kV route New 380/220 kV transformer in Chippis | 2022 | 4 | Delayed | ACTransmissionLine | Chamoson | Chippis | AC | None | 30 | 166 | 0.83 | +/- 10 % | ++ | ++
1472 | St. Peter (AT) - Tauern (AT) | 312 | new 380-kV-Line | 2025 | 4 | Delayed | ACTransmissionLine | St. Peter | Tauern | AC | None | 128 | 890 | 4 | 10% | ++ | ++ |  |  |  |  | 43 | None
1685 | Dollern - Stade | 1043 | New 380kV double circuit OHL Dollern - Stade including new 380kV switchgear in Stade. Length 14km. | 2021 | 4 | Delayed | ACTransmissionLine | Dollern (DE) | Stade (DE) | AC | None | 14 | 20 | 0.2 | -0.1
144 | Audorf - Kassoe | 39 | Step 3 in the Danish-German agreement to upgrade the Jutland-DE transfer capacity. It consists of a new 400kV route in Denmark and In Germany new 400kV line mainly in the trace of a existing 220kV line. | 2020 | 4 | Investment on time | ACTransmissionLine | Audorf (DE) | Kassoe (DK) | AC | None | 110 | 536 | 4 |  | ++ | ++
1500 | 1. SK-HU interconnection | 48 | "New interconnection (new 2x400 kV tie-line) between SK and HU starting from Gabcikovo substation (SK) to the Gonyu substation (HU), with one circuit connected to Velky Dur (SK) substation. Project does not include the erection of new switching station Gabcikovo next to the existing one. It includes extension of the new Gabcikovo substation by the two 400 kV bays where the new double line will be connected." | 2020 | 4 | Investment on time | ACTransmissionLine | Gabcikovo (SK) | Gonyu (HU) | AC | None | 110 | 27.65 | 0.7308 | ±10% | ++ | ++
1501 | 2. SK-HU interconnection | 48 | Connection of the two existing substations Rimavska Sobota (SK) - Sajoivanka (HU) by the new double 400 kV OHL armed only with one circuit on the both sides. | 2020 | 4 | Investment on time | ACTransmissionLine | Rimavska Sobota (SK) | Sajoivanka (HU) | AC | None | 48 | 51.38 | 0.6904 | ±10% | ++ | ++
386 | 3rd EE-LV interconnection | 62 | "330 kV AC OHL between Kilingi-Nomme substation in Estonia and Riga CHP2 substation in Latvia. New 330 kV power transmission line is planned to take route along already existing 110 kV power transmission lines, by constructing both 110 kV and 330 kV lines on the same towers. Under the framework of the project it is planned to reconstruct the open-air switchyard of the 330/110 kV substation Riga CHP2 by constructing new open-air connection point for the 330 kV line Kilingi Nomme - Riga CHP2. """ | 2020 | 4 | Investment on time | ACTransmissionLine | Kilingi-Nomme (EE) | Riga CHP2 (LV) | AC | None | 205 | 120 | 0.6 | 10 | ++ | ++
735 | Harku-Sindi 330kV OHL | 62 | New double circuit OHL with 2 different voltages 330 kV and 110 kV and with capacity 1143 MVA/240 MVA and a length 175 km. Major part of new internal connection will be established on existing right of way on the western part of Estonian mainland.The investment helps together with 3rd EE-LV interconnector to increase interarea capacity up to 600 MW. | 2021 | 4 | Investment on time | ACTransmissionLine | Harku (EE) | Sindi (EE) | AC | None | 175 | 60 | 0.1145 |  | ++ | ++
1062 | Riga CHP2 - Riga HPP | 62 | The internal reinforcement for 3rd EE-LV interconnector and significant investment for Baltic Synchronization project | 2020 | 4 | Investment on time | ACTransmissionLine | Riga CHP2 (LV) | Riga HPP (LV) | AC | None | 15 | 20 | 0.1 | 10 | ++ | ++
373 | Ostroleka-Stanislawow | 123 | Construction of new 400 kV AC double-circuit OHL line with a length of 108 km and capacity of 2x2450 MVA between Ostroleka and Stanislawow. | 2023 | 4 | Investment on time | ACTransmissionLine | Ostroleka (PL) | Stanislawow (PL) | AC | None | 108 | 79.7 | 1 |  | ++ | ++
96 | 96 | 127 | New 30km single circuit 400kV OHL between the future substations of Deliceto and Bisaccia, in the Candela area | 2021 | 4 | Investment on time | ACTransmissionLine | Deliceto (IT) | Bisaccia (IT) | AC | None | 30 | 190 | 1.74 |  | ++ | ++ |  | 22 | Other | - | 0 | None
800 | 400 kV OHL Varna-Burgas | 138 | New 86 km single circuit 400kV OHL in parallel to the existing one. | 2021 | 4 | Investment on time | ACTransmissionLine | Varna(BG) | Burgas(BG) | AC | None | 86 | 63 | 0.8 | +10%, -10% | ++ | ++ |  | 7 | HabitatsDirective
262 | 262 | 142 | New 400kV OHL. Line lengt 150km. | 2021 | 4 | Investment on time | ACTransmissionLine | Maritsa East 1 (BG) | Burgas (BG) | AC | None | 150 | 80 | 1.1 | +10%, -10% | ++ | ++
886 | 886 - east of Austria | 186 | To allow the grid integration of the planned renewable energy generation (mainly wind power) in the north-eastern part of Austria ("Weinviertel") and to cover the foreseen load growth in that region the transmission grid infrastructure has to be enforced and new substations for the connection needs to be erected | 2022 | 4 | Investment on time | ACTransmissionLine | Seyring | Zaya | AC | None | 60 | 215 | 1 | 10 | ++ | ++ |  |  |  |  | 31 | None
742 | Pyhanselka-Petajavesi | 197 | New single circuit 400 kV OHLs will be built from middle Finland to Oulujoki Area to increase the capacity between North and South Finland. Substations to connect wind farms in the region are also in consideration. | 2022 | 4 | Investment on time | ACTransmissionLine | Pyhanselka (FI) | Petajavesi (FI) | AC | None | 300 | 100 | 0.242 | -0.1 | ++ | ++
1684 | Conneforde-Wilhelmshaven | 207 | New 380kV double circuit (OHL, partly underground) Conneforde - Wilhelmshaven (Fedderwarden, former Maade) including new 380kV switchgear Fedderwarden. Length 35 km. | 2020 | 4 | Investment on time | ACTransmissionLine | Conneforde (DE) | Wilhelmshaven (DE) | AC | None | 30 | 140 | 1.1 | -0.1 | ++ | ++
1527 | 400 kV OHL Kragujevac-Kraljevo | 227 | 400 kV OHL Kragujevac-Kraljevo | 2020 | 4 | Investment on time | ACTransmissionLine | SS Kragujevac | SS Kraljevo | AC | None | 60 | 17 | 0.2 | 5% | ++ | ++
1246 | Upgrade Meeden - Diele | 245 | Increase of the interconnection capacity between The Netherlands and Germany by adding one new phase shifting transformer and apply dynamic line rating on the existing 380 kV double circuit tie line between Meeden and Diele. | 2021 | 4 | Investment on time | ACTransmissionLine | Meeden [NL] | Diele [DE] | AC | None | 27 | 38 | 0.4 | +/- 10% | ++ | ++
667 | Heide/West - Klixbüll | 258 | About 135 km new 380-kV-lines and around 10 new transformers for integration of onshore Wind in Schleswig-Holstein and increase of NTC between DE and DK | 2022 | 4 | Investment on time | ACTransmissionLine | Brunsbüttel (DE) | Klixbüll (DE) | AC | None | 125 | 360 | 2.9 | -0.1 | ++ | ++
445 | BRABO II: Zandvliet - Lillo - Liefkenshoek | 297 | The second phase of the BRABO project consists of the construction of a new double circuit 380kV overhead line from Zandvliet via Lillo to Liefkenshoek where the new line will be the temporarily connected to the existing 380kV line Doel-Mercator.This new line will be constructed making use of the corridor of the existing 150kV overhead line Zandvliet-Oorderen-Lillo, which will be undergrounded. | 2020 | 4 | Investment on time | ACTransmissionLine | Zandvliet | Lillo - Liefkenshoek | AC | None | 18 | 100 | 0.1 | 5% | ++ | ++ |  | 1.5 1 | HabitatsDirective BirdsDirective
1558 | Double 400 kV OHL Cirkovce(SI)-Heviz(HU)/Zerjavinec(HR) | 320 | New double circuit 400kV overhead line in Slovenia (section Cirkovce-Pince) and a new 400 kV substation Cirkovce (SI). The new OHL will be connected to one circuit of the existing double circuit 400kV OHL Heviz(HU)-Zerjavinec(HR), creating two new cross-border lines: Heviz(HU)-Cirkovce(SI) and Cirkovce (SI)-Zerjavinec (HR). | 2021 | 4 | Investment on time | ACTransmissionLine | Cirkovce (SI) | Heviz (HU) \ Zerjavinec (HR) | AC | None | 80 | 132.5 | 0.12 | +/- 5% | ++ | ++ |  | 28 | OtherNatureProtectionAreasUnderNationalLaw |  | 37 | OtherNatureProtectionAreasUnderNationalLaw
1686 | Wahle - Mecklar | 1043 | New 380kV double circuit OHL Wahle - Mecklar including two new substations. Length: 210km. | 2024 | 4 | Investment on time | ACTransmissionLine | Wahle (DE) | Mecklar (DE) | AC | None | 210 | 610 | 4.9 | -0.1
1556 | Prati (IT) – Steinach (AT) | 336 | New Italy-Austria tie-line between the existing 110kV Steinach substation in Austria and 132 kV Brennero substation, including PST; and connection to 132 kV Prati di Vizze substation." | 2023 | 4 | New Investment | ACTransmissionLine | Prati di Vizze (IT) | Steinach (AT) | AC | None | 139 | 40 | 0.6 |  | ++ | ++
1622 | 400kV OHL SS Bitola - SS Elbasan | 350 | New 150km cross-border single circuit 400kV OHL between existing substation Bitola(Macedoonia) and Elbasan(Albania). | 2020 | 4 | New Investment | ACTransmissionLine | Bitola | Elbasan | AC | None | 161 | 63.733 | 2.867 |  | ++ | ++
1716 | Interconnection between Crete and Peloponnese (Phase I) | 1055 | New 150 kV AC double circuit submarine and underground cables between Crete and Peloponnese | 2020 | 4 | New Investment | ACTransmissionLine | Chania I | Molai (through Sklavouna Terminal) | AC | None | 179 | 356.42 | 1.2 | 9 |  |  |  | 25 11 2 | HabitatsDirective BirdsDirective OtherNatureProtectionAreasUnderNationalLaw |  | 9.63 | HabitatsDirective
60 | FR-BE I: Avelin/Mastaing-Avelgem-Horta HTLS | 23 | Replacement of the current conductors on the axis Avelin/Mastaing - Avelgem - Horta with high performance conductors (HTLS = High Temperature Low Sag) | 2022 | 4 | Rescheduled | ACTransmissionLine | Avelin/Mastaing (FR) | Horta (BE) | AC | None | 80 | 165 | 0.4 | 5% | ++ | ++ |  | 3 | HabitatsDirective |  | 35 | HabitatsDirective
614 | Reschenpass Interconnector | 26 | interconnector IT-AT | 2023 | 4 | Rescheduled | ACTransmissionLine | Nauders (AT) | Glorenza (IT) | AC | None | 26 | 175 | 2.5 | 10 | ++ | 0 |  | 0 | None |  | 2 | Other | -
1488 | Diemen-Lelystad-Ens | 103 | Upgrade of existing 380kV circuits between Diemen, Lelystad and Ens from 2* 2,5 kA to 2* 4kA circuits by replacing the conductors with HTLS conductors | 2022 | 4 | Rescheduled | ACTransmissionLine | Diemen | Ens | AC | None | 75 | 105 | 1 | +/- 10% | ++ | ++
258 | 258 | 142 | New 13km single circuit 400kV OHL in parallel to the existing one. | 2021 | 4 | Rescheduled | ACTransmissionLine | Maritsa East 1 (BG) | Maritsa East 3 (BG) | AC | None | 13 | 7.4 | 0.1 | +10%, -10% | ++ | ++
1546 | NoordWest380 | 348 | Upgrade of existing 220kV circuits between Eemshaven and Vierverlaten to 2* 380kV – 2645MVA circuits; New 380kV substation Vierverlaten | 2023 | 4 | Rescheduled | ACTransmissionLine | Eemshaven Oude Schip | Vierverlaten | AC | None | 40 | 411 | 2.1 | 10% | ++ | ++ | + | [6 empty] | More info: https://www.rvo.nl/onderwerpen/bureau-energieprojecten/lopende-projecten/hoogspanning/eemshaven-os-vierverlaten-380-kv
1731 | ZuidWest380 West | 1063 | New 380 kV substation Rilland; New 380 kV double circuit line 2645MVA between Borssele and Rilland; Upgrade of existing 380 kV line Borssele-Geertruidenberg to 1975MVA. | 2022 | 4 |  | ACTransmissionLine | Borssele | Rilland | AC | None | 40 | 564 | 2.8 | 10 | [9 empty] | More info: https://www.rvo.nl/onderwerpen/bureau-energieprojecten/lopende-projecten/hoogspanning/zuid-west-380-kv-west
146 | ALEGrO | 92 | "Connection between the Oberzier substation in Germany and the Lixhe substation in Belgium via a +-100 km HVDC underground cable, including 2 DC/AC convertor stations to integrate the DC cable with the AC substations at Lixhe & Oberzier." | 2020 | 4 | Investment on time | DCTransmissionLine | Oberzier (DE) | Lixhe (BE) | DC | Monopolar | 90 | 560 | 4.2 | 6% | ++ | ++ |  | 2 | HabitatsDirective |  | 48 | HabitatsDirective
1487 | ElecLink | 172 | ElecLink is a new FR – UK interconnection cable with 1000 MW capacity through the Channel Tunnel between Sellindge (UK) and Mandarins (FR). Converter stations will be located on Eurotunnel concession at Folkestone and Coquelles. This HVDC interconnection is a PCI project (Project of Common Interest) no. 1.7.3 | 2021 | 4 | Investment on time | DCTransmissionLine | Sellindge (UK) | Mandarins (FR) | DC | None | 69 | 580 | 4.5 | 20% | ++ | ++ | +
1503 | Second HVDC Module IT-ME | 28 | Second HVDC Module (600 MW) of interconnection line between Italy and Montenegro via 445 km 500kV DC subsea cable and converter stations at both ending points. | 2026 | 4 | Rescheduled | DCTransmissionLine | Villanova (IT) | Lastva (ME) | DC | Bipolar | 445 | 362 | 0.7 | 10 | ++ | ++ |  | 0 | None |  | 0 | None
141 | Kriegers Flak CGS | 36 | Four offshore windfarms connected to shore combined with 400 MW interconnection between both countries. New technical solution connecting 220 and 150 kV AC offshore grid and onshore HVDC VSC Back-to-Back Converter. | 2020 | 4 | Delayed | OffshoreACTransmissionCable | Ishøj / Bjæverskov (DK) | Bentwisch (DE) | AC | None | 24 | 320 | 16 | 20 | ++ | 0
142 | Norway - Germany HVDC | 37 | A 623 km 500 kV HVDC interconnector between southern Norway and northern Germany. 514 km of the interconnector is subsea | 2020 | 4 | Investment on time | OffshoreDCTransmissionCable | Tonstad (NO) | Wilster (DE) | DC | None | 623 | 1850 | 15 |  | ++ | ++ | +
424 | Norway - Great Britain | 110 | A 720 km long 515 kV 1400 MW HVDC subsea interconnector between western Norway and eastern England. | 2021 | 4 | Investment on time | OffshoreDCTransmissionCable | Kvilldal (NO) | Blyth (GB) | DC | Bipolar | 720 | 1658.6 | 23.2 |  | ++ | ++ | + |  | None
998 | Viking Link DKW-GB, TYNDP ID 167.998 | 167 | 2 x700 MW HVDC subsea link across the North Seas. New substations on both sides; Bicker Fen (GB); Revsing (DK) | 2023 | 4 | Investment on time | OffshoreDCTransmissionCable | Revsing (DKW) | Bicker Fen (GB) | DC | None | 770 | 1655 | 16 |  | ++ | ++ | +
1712 | R Vitkov | 200 | A construction of a new 400/110 kV substation GIS technology equipped with two transformers with nominal capacity of 2x350 MVA | 2021 | 4 | Ahead of time | OnshoreSubstation | Vitkov (CZ) | N/A | AC | None | 0 | 27.43 | 0.063 | -10%, +15% | ++ | ++ | [7 empty] | In accordance with the European and Czech EIA legislation all over-headline projects (investment items 308, 309 and 314) have undergone screening and full scoping EIA assessment and were granted approval opinion by the competent authority, the Ministry of Environment of the Czech Republic. All investment items are included in the Czech Land Use Development Policy which is the land use plan for the entire country adopted on 15th April 2015 by the Czech government under the governmental resolution. The proposed routes (corridor) of the over-headlines were chosen with respect to the municipalities' land plans, transport and technical infrastructures and other development plans of regional importance (local roads, highways, railways, other transport and technical infrastructures). For the purpose of finding a suitable route, a spatial – land oriented technical studies were carried out that evaluated several route variants with consideration of several aspects including environmental ones. The proposed routes were then communicated with relevant and respective local and regional authorities, municipalities and other technical infrastructure owners. The outputs from the above studies were taken as an important input into the environment impact assessment which concluded the projects not to have negative NATURA 2000 sites and were granted an EIA approval.
715 | 220kV Stalpu substation upgrade to 400 kV | 138 | To reinforce the cross-section between the Black Sea coast wind generation in Romania and Bulgaria and the consumption and storage centers to the West, the 220 kV OHL Stalpu-Teleajen-Brazi is upgraded to 400 kV, as a continuation of the 400 kV d.c. OHL Cernavoda-Stalpu. The 220/110 kV substation Stalpu is upgraded to 400/110kV (1x250MVA). | 2023 | 4 | Delayed | OnshoreSubstation | Stalpu (RO) | Stalpu (RO) | AC | None | 0 | 15 | 0.15 | -5%, +5% | ++ | ++ |  | 0 | None |  | 0 | None
701 | 400 kV Substation Resita | 144 | New 400 kV substation Resita (T400/220 kV 400 MVA + T 400/110 kV 250 MVA), as development of the existing 220/110 kV substation. | 2025 | 4 | Delayed | OnshoreSubstation | Resita (RO) | Resita (RO) | AC | None | 0 | 24 | 0.24 | -5%, +5% | ++ | ++ |  | 0 | None |  | 0 | None
1711 | R Kocin | 200 | Upgrade and extension of the existing 400/110 kV substation, increasing nominal capacity of transformers from 2x250 MVA to 2x350 MVA | 2023 | 4 | Investment on time | OnshoreSubstation | Kocin (CZ) | N/A | AC | None | 0 | 139.87 | 0.06 | -10%, +15% | ++ | ++ | [7 empty] | In accordance with the European and Czech EIA legislation all over-headline projects (investment items 308, 309 and 314) have undergone screening and full scoping EIA assessment and were granted approval opinion by the competent authority, the Ministry of Environment of the Czech Republic. All investment items are included in the Czech Land Use Development Policy which is the land use plan for the entire country adopted on 15th April 2015 by the Czech government under the governmental resolution. The proposed routes (corridor) of the over-headlines were chosen with respect to the municipalities' land plans, transport and technical infrastructures and other development plans of regional importance (local roads, highways, railways, other transport and technical infrastructures). For the purpose of finding a suitable route, a spatial – land oriented technical studies were carried out that evaluated several route variants with consideration of several aspects including environmental ones. The proposed routes were then communicated with relevant and respective local and regional authorities, municipalities and other technical infrastructure owners. The outputs from the above studies were taken as an important input into the environment impact assessment which concluded the projects not to have negative NATURA 2000 sites and were granted an EIA approval.
1528 | Upgrade of SS Kraljevo | 227 | Upgrade of SS Kraljevo | 2020 | 4 | Investment on time | OnshoreSubstation | SS Kraljevo | SS Kraljevo | AC | None | 0 | 10.5 | 0.13 | 5% | ++ | ++
605 | BRABO II: Lillo 380 | 297 | "This concerns the construction of the 380kV substation Lillo, including a 380/150 kV transformer, as part of the second phase of the BRABO-project." | 2019 | 4 | Investment on time | OnshoreSubstation | Lillo (BE) | Lillo (BE) | AC | None | 0 | 15 | 0.1 | 5% | ++ | ++ |  |  |  |  | 15.5 | HabitatsDirective
1623 | 400 kV SS Ohrid | 350 | New 400/110 kV substation in Ohrid area connected in/out to the new 400 kV line Bitola-Elbasan. This SS will contribute to the security of supply in the internal southern network of the country. | 2020 | 4 | New Investment | OnshoreSubstation | missing value | missing value | AC | None | 0 | 17.68 | 1.414 |  | ++ | ++
1493 | PST Vierraden | 94 | Installation of new PSTs in Vierraden | 2022 | 4 | Delayed | PhaseShiftingTransformer | Vierraden | Vierraden | AC | None | 0 | 110.8 | 2 |  | ++ | ++
1281 | Aubange-Moulaine: PSTs | 173 | "Investment consists of the installation of two phase shifting transformers in Aubang, one on each of the 225kV circuits of the Aubange-Moulaine interconnector." | 2021 | 4 | Investment on time | PhaseShiftingTransformer | Aubange (BE) | Moulaine (FR) | AC | None | 0 | 20 | 0.1 | 5%
1257 | Belgium-Netherlands: Zandvliet-Rilland | 262 | Upgrade of the capacity of the cross-border lines by replacing the current conductors with high performance (HTLS) conductors combined with the installation of additional phase shifting transformers in Zandvliet. | 2022 | 4 | Investment on time | PhaseShiftingTransformer | Zandvliet (BE) | Rilland (NL) | AC | None | 10 | 60 | 0.1 | 10% | ++ | ++ |  | 2 2 | HabitatsDirective BirdsDirective |  | 7 | HabitatsDirective
696 | Hunew 1 | 48 | 2x70 Mvar shunt reactors in station Sajóivánka (HU) | 2020 | 4 | Investment on time | ReactiveCompensationDevice | Sajóivánka (HU) | N/A | AC | None | 0 | 0.5 | 0.0097 | ±10% | ++ | ++
697 | Hunew 2 | 48 | Second 400/120 kV transformer in station Sajóivánka (HU) | 2020 | 4 | Investment on time | Transformer | Sajóivánka (HU) | N/A | AC | None | 0 | 2.1 | 0.0387 | ±10% | ++ | ++
1566 | Reconstructions in North Eastern Lithuania | 170 | Utenos TP substations and 330/1110/10 kV Ignalinos AE TP substations reconstruction. Relocation of HV equipment (from 330/110/10 kV Ignalinos AE TP substation to 330/110/10 kV Lietuvos E TP substation) and changing topology of 330 kV overhead lines | 2021 | 4 | Investment on time |  | - | - | AC | None | 0 | 24.26 | 0.024 | +5%, - 5% | ++ | ++
1568 | Upgrades in Alytus substation (LT) | 170 | Construction of three new 400/330 kV autotransformers in Alytus substation, to make LT-PL border operation in AC mode. | 2021 | 4 | Investment on time |  | Alytus | - | AC | None | 0 | 22.44 | 0.022 | +5%, - 5% | ++ | ++
1565 | Reconstruction of 330 kV OHL LE-Vilnius | 170 | Reconstruction of 330 kV OHL LE-Vilnius from single-circuit into double-circuit | 2020 | 6 | Investment on time | ACTransmissionLine | Lietuvos E | Vilnius | AC | None | 41 | 19.3 | 0.019 | +5%, - 5% | ++ | ++