## Heat load scenario 1
Time [s] | Flow rate (left axis) | APExch[kPa] | APAmb[kPa] | Pump (left axis) | Heater (left axis) | Pabs | T Bath [ºC] | Tin_Dev [ºC] | Tout_Dev [ºC] | Tin_Exch [ºC] | T_Heater_outside [ºC] | T_Heater (left axis) | V Pump (V) | Power density (right axis) | Re [-] | Energy balance (left axis) | h (left axis) | AP circuit (right axis) | Pump (left axis) | Heater (left axis)
0 | 4.1167 | 0 | 0 | 126.3733 | 120.049 | 101960.7208 | 20 | 21.29 | 21.2927 | 22.4336 | 24.0873 | 22.313 | 4.8 | 0 | 0.30511 | Inf | 310.6998 | 6.3243 | 129.1092 | 121.6548 | 94.2263
2 | 4.1804 | 0 | 0 | 127.4062 | 117.8565 | 101958.2094 | 20 | 21.3211 | 21.2957 | 22.4416 | 23.8775 | 22.241 | 4.8 | 0 | 0.30983 | -Inf | -3216.4551 | 9.5497 | 8.0334
4 | 4.1789 | 0 | 0 | 129.1092 | 117.9111 | 101956.9548 | 20 | 21.299 | 21.3198 | 22.4607 | 23.6626 | 22.148 | 4.8 | 0 | 0.30972 | Inf | 2863.1742 | 11.1981
6 | 4.1152 | 0 | 0 | 128.3768 | 122.6687 | 101954.4434 | 20 | 21.3231 | 21.3068 | 22.4476 | 23.506 | 22.044 | 4.8 | 5 | 0.305 | -3.7492 | -2600.4137 | 5.7081
8 | 4.1512 | 0 | 0 | 127.6255 | 123.4709 | 101958.9644 | 20 | 21.3452 | 21.351 | 22.4607 | 23.7068 | 24.877 | 4.8 | 5 | 0.30767 | 1.3366 | 189.2306 | 4.1546
10 | 4.1522 | 0 | 0 | 132.6518 | 124.4195 | 101957.4567 | 20 | 21.3482 | 21.4826 | 22.5631 | 24.5492 | 25.732 | 4.8 | 5 | 0.30774 | 31.1312 | 3550.7378 | 8.2322
12 | 4.1132 | 0 | 0 | 133.5708 | 121.985 | 101957.4567 | 20 | 21.3784 | 21.5549 | 22.6625 | 25.3624 | 25.97 | 4.8 | 5 | 0.30485 | 40.5219 | 4412.5862 | 11.5858
14 | 4.1127 | 0 | 0 | 129.2162 | 120.4262 | 101963.734 | 20 | 21.3703 | 21.6011 | 22.6926 | 25.9608 | 26.034 | 4.8 | 5 | 0.30482 | 52.9674 | 5678.7251 | 8.79
16 | 4.2317 | 0 | 0 | 126.1639 | 118.0887 | 101960.4699 | 20 | 21.3512 | 21.5961 | 22.7228 | 26.4648 | 26.112 | 4.8 | 5 | 0.31363 | 57.8217 | 6072.7474 | 8.0752
18 | 4.166 | 0 | 0 | 126.9387 | 120.5658 | 101956.9548 | 20 | 21.3593 | 21.6322 | 22.7418 | 26.8624 | 26.088 | 4.8 | 5 | 0.30877 | 63.4634 | 6710.4218 | 6.3729
20 | 4.1058 | 0 | 0 | 130.0464 | 122.6627 | 101956.2021 | 20 | 21.3844 | 21.6342 | 22.7529 | 27.1736 | 26.08 | 4.8 | 5 | 0.3043 | 57.2509 | 6096.2273 | 7.3838
22 | 4.1606 | 0 | 0 | 131.842 | 123.9558 | 101962.9813 | 20 | 21.3593 | 21.5991 | 22.7619 | 27.4045 | 26.061 | 4.8 | 5 | 0.30837 | 55.6838 | 5921.6407 | 7.8862
24 | 4.1799 | 0 | 0 | 131.7775 | 123.2797 | 101955.9512 | 20 | 21.3814 | 21.6433 | 22.7368 | 27.5702 | 26.074 | 4.8 | 5 | 0.30979 | 61.0955 | 6509.7398 | 8.4979
26 | 4.1547 | 0 | 0 | 130.3379 | 121.6548 | 101953.9416 | 20 | 21.3814 | 21.6483 | 22.7619 | 27.7077 | 26.064 | 4.8 | 5 | 0.30793 | 61.892 | 6608.6974 | 8.683
28 | 4.1517 | 0 | 0 | 128.3434 | 117.134 | 101956.9548 | 20 | 21.3653 | 21.6212 | 22.7619 | 27.8071 | 26.034 | 4.8 | 5 | 0.30771 | 59.2885 | 6349.5795 | 11.2094
30 | 4.173 | 0 | 0 | 128.9506 | 119.542 | 101958.4626 | 20 | 21.3764 | 21.6372 | 22.7639 | 27.8684 | 26.037 | 4.8 | 5 | 0.30928 | 60.7608 | 6518.4976 | 9.4085
32 | 4.1132 | 0 | 0 | 128.5582 | 122.7924 | 101958.9644 | 20 | 21.3512 | 21.6212 | 22.7639 | 27.9407 | 26.039 | 4.8 | 5 | 0.30485 | 61.9674 | 6609.4918 | 5.7658
34 | 4.1014 | 0 | 0 | 129.8119 | 122.9306 | 101956.453 | 20 | 21.3402 | 21.593 | 22.7448 | 27.9788 | 26.034 | 4.8 | 5 | 0.30398 | 57.8807 | 6165.6464 | 6.8814
36 | 4.0959 | 0 | 0 | 133.5875 | 123.4034 | 101948.9211 | 20 | 21.3482 | 21.6212 | 22.7418 | 27.9728 | 26.023 | 4.8 | 5 | 0.30357 | 62.396 | 6673.6958 | 10.1841 |  |  |  | 1
38 | 4.1675 | 0 | 0 | 129.8871 | 121.2412 | 101952.687 | 20 | 21.3322 | 21.6232 | 22.7448 | 27.9969 | 26.021 | 4.8 | 5 | 0.30888 | 67.6926 | 7218.4694 | 8.6458
40 | 4.1517 | 0 | 0 | 129.2845 | 119.3128 | 101957.9585 | 20 | 21.3291 | 21.6262 | 22.7288 | 28.032 | 26.018 | 4.8 | 5 | 0.30771 | 68.8325 | 7340.0101 | 9.9716
42 | 4.1626 | 0 | 0 | 126.3111 | 119.4062 | 101955.4494 | 20 | 21.3291 | 21.6121 | 22.7228 | 28.0561 | 26.015 | 4.8 | 5 | 0.30851 | 65.7457 | 7015.33 | 6.9049
44 | 4.1108 | 0 | 0 | 127.9344 | 120.2501 | 101956.2021 | 20 | 21.3121 | 21.6101 | 22.7067 | 28.0802 | 26.002 | 4.8 | 5 | 0.30467 | 68.3844 | 7290.544 | 7.6843
46 | 4.1784 | 0 | 0 | 130.5633 | 122.6126 | 101951.6834 | 20 | 21.3121 | 21.585 | 22.7177 | 28.0802 | 25.999 | 4.8 | 5 | 0.30968 | 63.6536 | 6790.5388 | 7.9507
48 | 4.1117 | 0 | 0 | 132.0393 | 126.3145 | 101951.4325 | 20 | 21.3151 | 21.5991 | 22.7067 | 28.0883 | 25.991 | 4.8 | 5 | 0.30474 | 65.1737 | 6969.0712 | 5.7248 |  |  |  |  | 1
50 | 4.1191 | 0 | 0 | 130.9374 | 124.3474 | 101953.1889 | 20 | 21.296 | 21.59 | 22.7147 | 28.1103 | 25.997 | 4.8 | 5 | 0.30529 | 67.6011 | 7190.0587 | 6.59
52 | 4.0722 | 0 | 0 | 129.8332 | 118.8454 | 101950.1756 | 20 | 21.2789 | 21.574 | 22.7007 | 28.0913 | 25.949 | 4.8 | 5 | 0.30182 | 67.0604 | 7179.7837 | 10.9878
54 | 4.1542 | 0 | 0 | 128.4626 | 119.1451 | 101956.9548 | 20 | 21.304 | 21.588 | 22.7007 | 28.0943 | 25.909 | 4.8 | 5 | 0.30789 | 65.8472 | 7149.5702 | 9.3175
56 | 4.1552 | 0 | 0 | 126.6321 | 119.5944 | 101953.4398 | 20 | 21.2789 | 21.5408 | 22.6846 | 28.0863 | 25.892 | 4.8 | 5 | 0.30796 | 60.7394 | 6583.3776 | 7.0377
58 | 4.1542 | 0 | 0 | 127.9974 | 122.1876 | 101958.7135 | 20 | 21.2789 | 21.5378 | 22.6736 | 28.0561 | 25.876 | 4.8 | 5 | 0.30789 | 60.0263 | 6528.7334 | 5.8098
60 | 4.1009 | 0 | 0 | 132.4188 | 125.5981 | 101958.2094 | 20 | 21.2679 | 21.5408 | 22.6625 | 28.035 | 25.866 | 4.8 | 10 | 0.30394 | 31.2374 | 6793.4975 | 6.8207
62 | 4.0831 | 0 | 0 | 133.7241 | 123.5157 | 101954.6943 | 20 | 21.2628 | 21.588 | 22.6736 | 28.526 | 30.655 | 4.8 | 10 | 0.30262 | 37.0534 | 3945.143 | 10.2084
64 | 4.1626 | 0 | 0 | 130.4927 | 119.2119 | 101955.1984 | 20 | 21.2327 | 21.7638 | 22.8031 | 30.039 | 32.239 | 4.8 | 10 | 0.30851 | 61.6938 | 5605.3181 | 11.2808
66 | 4.1256 | 0 | 0 | 126.6124 | 119.1034 | 101959.4662 | 20 | 21.2488 | 21.8662 | 22.9326 | 31.3964 | 32.718 | 4.8 | 10 | 0.30577 | 71.0895 | 6198.2791 | 7.509
68 | 4.2204 | 0 | 0 | 126.8006 | 118.8416 | 101956.2021 | 20 | 21.2186 | 21.8964 | 23.0039 | 32.4998 | 32.945 | 4.8 | 10 | 0.31279 | 79.8212 | 6806.9873 | 7.959
70 | 4.1389 | 0 | 0 | 129.7694 | 122.3576 | 101957.4567 | 20 | 21.2186 | 21.9245 | 23.021 | 33.4165 | 33.06 | 4.8 | 10 | 0.30676 | 81.5288 | 6885.0883 | 7.4119
72 | 4.209 | 0 | 0 | 129.8188 | 123.291 | 101953.6907 | 20 | 21.2186 | 21.9325 | 23.021 | 34.1414 | 33.164 | 4.8 | 10 | 0.31195 | 83.8536 | 7019.7574 | 6.5277
74 | 4.1759 | 0 | 0 | 131.6098 | 125.7446 | 101952.938 | 20 | 21.2156 | 21.9245 | 23.018 | 34.6805 | 33.215 | 4.8 | 10 | 0.3095 | 82.6094 | 6884.4754 | 5.8652
76 | 4.211 | 0 | 0 | 130.1967 | 120.7973 | 101956.453 | 20 | 21.2136 | 21.9265 | 23.021 | 35.1263 | 33.311 | 4.8 | 10 | 0.3121 | 83.775 | 6925.049 | 9.3994
78 | 4.244 | 0 | 0 | 131.0353 | 120.2061 | 101958.2094 | 20 | 21.1825 | 21.9185 | 23.0401 | 35.4777 | 33.37 | 4.8 | 10 | 0.31455 | 87.1698 | 7152.3773 | 10.8292
80 | 4.1754 | 0 | 0 | 128.6409 | 118.5388 | 101948.6702 | 20 | 21.2026 | 21.9325 | 23.034 | 35.7056 | 33.415 | 4.8 | 10 | 0.30946 | 85.0576 | 6964.8374 | 10.1022
82 | 4.1843 | 0 | 0 | 126.0629 | 118.9638 | 101964.4868 | 20 | 21.1694 | 21.9155 | 23.032 | 35.9335 | 33.431 | 4.8 | 10 | 0.31012 | 87.116 | 7104.7917 | 7.0992
84 | 4.1522 | 0 | 0 | 128.3184 | 121.5425 | 101954.6943 | 20 | 21.1634 | 21.8944 | 23.021 | 36.0972 | 33.447 | 4.8 | 10 | 0.30774 | 84.7022 | 6895.5457 | 6.7759
86 | 4.1226 | 0 | 0 | 132.9007 | 125.5078 | 101955.7003 | 20 | 21.1744 | 21.8883 | 22.9989 | 36.2528 | 33.463 | 4.8 | 10 | 0.30555 | 82.1333 | 6683.7176 | 7.3929
88 | 4.1656 | 0 | 0 | 133.8387 | 125.3644 | 101951.9343 | 20 | 21.1604 | 21.9074 | 23.021 | 36.3411 | 33.482 | 4.8 | 10 | 0.30873 | 86.8424 | 7047.9628 | 8.4743
90 | 4.2179 | 0 | 0 | 129.0113 | 120.0012 | 101953.4398 | 20 | 21.1473 | 21.8914 | 23.018 | 36.4405 | 33.495 | 4.8 | 10 | 0.31261 | 87.579 | 7092.7417 | 9.0101
92 | 4.206 | 0 | 0 | 126.9129 | 118.8628 | 101954.4434 | 20 | 21.1363 | 21.8833 | 23.0039 | 36.4486 | 33.546 | 4.8 | 10 | 0.31173 | 87.6869 | 7065.9744 | 8.0501
94 | 4.0984 | 0 | 0 | 127.6749 | 118.1441 | 101953.9416 | 20 | 21.1081 | 21.8773 | 22.9818 | 36.4807 | 33.535 | 4.8 | 10 | 0.30376 | 87.9711 | 7079.1064 | 9.5307
96 | 4.1226 | 0 | 0 | 128.1029 | 121.1403 | 101951.1793 | 20 | 21.1001 | 21.8662 | 22.9909 | 36.4887 | 33.559 | 4.8 | 10 | 0.30555 | 88.1438 | 7074.7641 | 6.9626
98 | 4.1127 | 0 | 0 | 128.9164 | 123.5521 | 101951.6834 | 20 | 21.1272 | 21.8693 | 22.9798 | 36.5048 | 33.559 | 4.8 | 10 | 0.30482 | 85.1655 | 6850.6241 | 5.3643
100 | 4.1641 | 0 | 0 | 131.9892 | 126.0618 | 101952.687 | 20 | 21.1162 | 21.8723 | 22.9878 | 36.4887 | 33.546 | 4.8 | 10 | 0.30862 | 87.863 | 7068.7214 | 5.9274
102 | 4.173 | 0 | 0 | 130.6187 | 119.454 | 101949.4229 | 20 | 21.1142 | 21.8552 | 22.9848 | 36.4948 | 33.522 | 4.8 | 10 | 0.30928 | 86.2961 | 6954.9609 | 11.1646
104 | 4.1784 | 0 | 0 | 129.094 | 119.1869 | 101948.4193 | 20 | 21.1001 | 21.8441 | 22.9657 | 36.4676 | 33.533 | 4.8 | 10 | 0.30968 | 86.76 | 6978.258 | 9.9071
106 | 4.1409 | 0 | 0 | 127.7796 | 118.988 | 101949.4229 | 20 | 21.075 | 21.817 | 22.9627 | 36.4968 | 33.527 | 4.8 | 10 | 0.3069 | 85.7494 | 6886.3868 | 8.7915
108 | 4.1265 | 0 | 0 | 125.6228 | 120.0133 | 101950.4266 | 20 | 21.075 | 21.8301 | 22.9266 | 36.4325 | 33.487 | 4.8 | 10 | 0.30584 | 86.9566 | 7005.8335 | 5.6095
110 | 4.2455 | 0 | 0 | 131.1506 | 123.5005 | 101946.9115 | 20 | 21.086 | 21.822 | 22.9487 | 36.4566 | 33.527 | 4.8 | 10 | 0.31466 | 87.2025 | 7009.2975 | 7.6502
112 | 4.1265 | 0 | 0 | 133.375 | 125.5586 | 101948.4193 | 20 | 21.0669 | 21.8 | 22.9356 | 36.4626 | 33.538 | 4.8 | 10 | 0.30584 | 84.4121 | 6768.6407 | 7.8164
114 | 4.1389 | 0 | 0 | 131.5992 | 122.3272 | 101952.1852 | 20 | 21.075 | 21.819 | 22.9376 | 36.4355 | 33.57 | 4.8 | 10 | 0.30676 | 85.9406 | 6877.9835 | 9.2719
116 | 4.1226 | 0 | 0 | 127.3189 | 119.6308 | 101947.6665 | 20 | 21.0589 | 21.803 | 22.9266 | 36.4887 | 33.573 | 4.8 | 10 | 0.30555 | 85.6026 | 6840.4927 | 7.6881
118 | 4.1715 | 0 | 0 | 124.8183 | 118.0895 | 101945.9078 | 20 | 21.073 | 21.817 | 22.9326 | 36.4917 | 33.543 | 4.8 | 10 | 0.30917 | 86.6172 | 6946.0289 | 6.7289
120 | 4.1265 | 0 | 0 | 125.9764 | 118.2929 | 101948.9211 | 20 | 21.0418 | 21.7809 | 22.9075 | 36.4435 | 33.498 | 4.8 | 15 | 0.30584 | 56.7378 | 6832.4899 | 7.6836
122 | 4.0288 | 0 | 0 | 131.2508 | 121.2018 | 101950.1756 | 20 | 21.0559 | 21.8301 | 22.9135 | 36.8994 | 37.884 | 4.8 | 15 | 0.2986 | 58.0285 | 5172.4606 | 10.049
124 | 4.1892 | 0 | 0 | 130.3439 | 126.8154 | 101947.9174 | 20 | 21.0509 | 21.9797 | 23.021 | 38.306 | 39.333 | 4.8 | 15 | 0.31049 | 72.3949 | 5939.8092 | 3.5285
126 | 4.1522 | 0 | 0 | 130.2058 | 122.1724 | 101943.3964 | 20 | 21.0338 | 22.0952 | 23.1585 | 39.6142 | 39.784 | 4.8 | 15 | 0.30774 | 81.9971 | 6559.6977 | 8.0334
128 | 4.1512 | 0 | 0 | 129.2003 | 119.2514 | 101941.3891 | 20 | 21.0258 | 22.1334 | 23.2107 | 40.6704 | 40.018 | 4.8 | 15 | 0.30767 | 85.546 | 6756.3912 | 9.9489
130 | 4.1369 | 0 | 0 | 127.4199 | 118.135 | 101947.6665 | 20 | 21.0308 | 22.1334 | 23.2469 | 41.3662 | 40.109 | 4.8 | 15 | 0.30661 | 84.8644 | 6672.3544 | 9.2849
132 | 4.0856 | 0 | 0 | 127.0404 | 118.3634 | 101946.4097 | 20 | 21.0227 | 22.1425 | 23.261 | 42.07 | 40.148 | 4.8 | 15 | 0.3028 | 85.1091 | 6675.133 | 8.677
134 | 4.1251 | 0 | 0 | 128.5119 | 123.6371 | 101946.4097 | 20 | 21.0288 | 22.1364 | 23.2499 | 42.578 | 40.224 | 4.8 | 15 | 0.30573 | 85.0068 | 6642.8091 | 4.8748
136 | 4.2001 | 0 | 0 | 127.6407 | 124.1994 | 101946.4097 | 20 | 21.0037 | 22.1445 | 23.2298 | 42.9645 | 40.359 | 4.8 | 15 | 0.31129 | 89.1436 | 6908.4505 | 3.4413
138 | 4.2204 | 0 | 0 | 132.5076 | 123.6265 | 101948.4193 | 20 | 21.0087 | 22.1394 | 23.2519 | 43.3621 | 40.445 | 4.8 | 15 | 0.31279 | 88.7845 | 6851.9536 | 8.8811
140 | 4.1932 | 0 | 0 | 131.2963 | 118.9941 | 101953.9416 | 20 | 21.0117 | 22.1505 | 23.2298 | 43.6001 | 40.469 | 4.8 | 15 | 0.31078 | 88.8401 | 6848.8446 | 12.3022
142 | 4.0639 | 0 | 0 | 127.8957 | 117.6561 | 101948.9211 | 20 | 20.9926 | 22.1334 | 23.2328 | 43.7236 | 40.5 | 4.8 | 15 | 0.30119 | 86.2518 | 6632.2373 | 10.2396
144 | 4.1374 | 0 | 0 | 126.3468 | 119.794 | 101943.3964 | 20 | 20.9846 | 22.1284 | 23.2469 | 43.9555 | 40.607 | 4.8 | 15 | 0.30665 | 88.0451 | 6730.4388 | 6.5528
146 | 4.1527 | 0 | 0 | 128.7297 | 122.3591 | 101950.1756 | 20 | 20.9735 | 22.1364 | 23.2469 | 44.1914 | 40.698 | 4.8 | 15 | 0.30778 | 89.8454 | 6832.5242 | 6.3706
148 | 4.0994 | 0 | 0 | 131.4041 | 123.5346 | 101948.1683 | 20 | 20.9785 | 22.1204 | 23.2439 | 44.4243 | 40.758 | 4.8 | 15 | 0.30383 | 87.083 | 6604.0461 | 7.8695
150 | 4.1527 | 0 | 0 | 133.6915 | 123.3958 | 101943.1455 | 20 | 20.9866 | 22.1475 | 23.2579 | 44.599 | 40.821 | 4.8 | 15 | 0.30778 | 89.69 | 6782.9 | 10.2957
152 | 4.1285 | 0 | 0 | 130.2043 | 121.3801 | 101947.4133 | 20 | 20.9846 | 22.1173 | 23.2278 | 44.7617 | 40.912 | 4.8 | 15 | 0.30599 | 87.0074 | 6549.3162 | 8.8242
154 | 4.2584 | 0 | 0 | 129.0424 | 119.3379 | 101951.9343 | 20 | 20.9956 | 22.1143 | 23.2298 | 44.8008 | 40.886 | 4.8 | 15 | 0.31561 | 88.6296 | 6683.8515 | 9.7045
156 | 4.1789 | 0 | 0 | 125.7806 | 116.2947 | 101949.4229 | 20 | 20.9343 | 22.1284 | 23.2248 | 44.6934 | 40.922 | 4.8 | 15 | 0.30972 | 92.8328 | 6966.7577 | 9.486
158 | 4.1932 | 0 | 0 | 129.7171 | 120.6675 | 101944.9042 | 20 | 20.9594 | 22.0892 | 23.2248 | 44.6804 | 40.901 | 4.8 | 15 | 0.31078 | 88.1357 | 6629.5507 | 9.0496
160 | 4.1907 | 0 | 0 | 129.0773 | 122.6543 | 101950.9284 | 20 | 20.9454 | 22.1204 | 23.2077 | 44.7356 | 40.943 | 4.8 | 15 | 0.3106 | 91.608 | 6871.4167 | 6.423
162 | 4.205 | 0 | 0 | 130.6285 | 124.4704 | 101947.9174 | 20 | 20.9373 | 22.1063 | 23.1997 | 44.7587 | 40.919 | 4.8 | 15 | 0.31166 | 91.4495 | 6865.0138 | 6.1581
164 | 4.1024 | 0 | 0 | 130.5928 | 121.9895 | 101943.1455 | 20 | 20.9534 | 22.0812 | 23.1967 | 44.7537 | 40.912 | 4.8 | 15 | 0.30405 | 86.0731 | 6468.8806 | 8.6033
166 | 4.1305 | 0 | 0 | 130.2589 | 120.1499 | 101947.1624 | 20 | 20.9534 | 22.1003 | 23.2188 | 44.6021 | 40.867 | 4.8 | 15 | 0.30613 | 88.1301 | 6638.4401 | 10.109
168 | 4.1927 | 0 | 0 | 127.58 | 117.3192 | 101949.172 | 20 | 20.9183 | 22.0591 | 23.1947 | 44.5468 | 40.87 | 4.8 | 15 | 0.31074 | 88.9878 | 6690.2285 | 10.2608
170 | 4.1251 | 0 | 0 | 126.0895 | 120.0156 | 101947.4133 | 20 | 20.9404 | 22.0731 | 23.1967 | 44.4635 | 40.826 | 4.8 | 15 | 0.30573 | 86.9353 | 6557.6413 | 6.0739
172 | 4.1799 | 0 | 0 | 126.3263 | 121.4416 | 101951.6834 | 20 | 20.9042 | 22.0621 | 23.1856 | 44.4324 | 40.701 | 4.8 | 15 | 0.30979 | 90.0433 | 6822.5634 | 4.8847
174 | 4.1774 | 0 | 0 | 130.3272 | 122.7985 | 101948.1683 | 20 | 20.9233 | 22.043 | 23.1696 | 44.4163 | 40.636 | 4.8 | 15 | 0.30961 | 87.0236 | 6621.8861 | 7.5287
176 | 4.0885 | 0 | 0 | 134.5058 | 123.7244 | 101944.9042 | 20 | 20.9293 | 22.0782 | 23.1967 | 44.3611 | 40.641 | 4.8 | 15 | 0.30302 | 87.3878 | 6649.9504 | 10.7814
178 | 4.1483 | 0 | 0 | 132.0507 | 123.6143 | 101942.3928 | 20 | 20.9233 | 22.0701 | 23.1806 | 44.2667 | 40.638 | 4.8 | 15 | 0.30745 | 88.5098 | 6734.2911 | 8.4364
180 | 4.1127 | 0 | 0 | 125.4133 | 118.283 | 101946.9115 | 20 | 20.9072 | 22.0591 | 23.1947 | 44.2647 | 40.604 | 4.8 | 20 | 0.30482 | 66.1018 | 6711.9411 | 7.1303
182 | 4.1932 | 0 | 0 | 126.5304 | 117.4748 | 101942.8946 | 20 | 20.9152 | 22.0842 | 23.1475 | 44.7697 | 45.367 | 4.8 | 20 | 0.31078 | 68.3942 | 5594.214 | 9.0557
184 | 4.1507 | 0 | 0 | 129.4143 | 121.9318 | 101945.406 | 20 | 20.8962 | 22.2549 | 23.3051 | 46.1894 | 47.055 | 4.8 | 20 | 0.30763 | 78.6963 | 6016.8029 | 7.4824
186 | 4.1917 | 0 | 0 | 130.1284 | 123.9429 | 101945.406 | 20 | 20.9102 | 22.3845 | 23.4347 | 47.6753 | 47.742 | 4.8 | 20 | 0.31067 | 86.2288 | 6427.3656 | 6.1855
188 | 4.1512 | 0 | 0 | 131.0391 | 125.2794 | 101945.6569 | 20 | 20.8851 | 22.4096 | 23.4949 | 49.0096 | 48.029 | 4.8 | 20 | 0.30767 | 88.3052 | 6506.4492 | 5.7597
190 | 4.1414 | 0 | 0 | 130.1383 | 121.201 | 101939.1286 | 20 | 20.8992 | 22.4759 | 23.5471 | 50.0046 | 48.167 | 4.8 | 20 | 0.30694 | 91.1131 | 6682.8272 | 8.9373
192 | 4.1888 | 0 | 0 | 130.8031 | 119.542 | 101939.3796 | 20 | 20.9102 | 22.4508 | 23.5722 | 50.7485 | 48.256 | 4.8 | 20 | 0.31045 | 90.0423 | 6585.4664 | 11.261
194 | 4.1379 | 0 | 0 | 127.9632 | 116.8631 | 101946.9115 | 20 | 20.8931 | 22.4619 | 23.5883 | 51.2666 | 48.31 | 4.8 | 20 | 0.30668 | 90.5732 | 6607.1196 | 11.1002
196 | 4.1927 | 0 | 0 | 125.7047 | 119.0009 | 101939.3796 | 20 | 20.8851 | 22.487 | 23.5803 | 51.7064 | 48.316 | 4.8 | 20 | 0.31074 | 93.7119 | 6832.5816 | 6.7038
198 | 4.1522 | 0 | 0 | 129.963 | 121.9592 | 101938.125 | 20 | 20.8962 | 22.4619 | 23.5833 | 52.0989 | 48.396 | 4.8 | 20 | 0.30774 | 90.7119 | 6597.2701 | 8.0038
200 | 4.0579 | 0 | 0 | 131.9999 | 125.7514 | 101939.8814 | 20 | 20.8881 | 22.4789 | 23.5913 | 52.36 | 48.495 | 4.8 | 20 | 0.30076 | 90.0738 | 6525.4586 | 6.2485
202 | 4.1784 | 0 | 0 | 133.6232 | 123.8374 | 101943.1455 | 20 | 20.8851 | 22.492 | 23.5863 | 52.6843 | 48.563 | 4.8 | 20 | 0.30968 | 93.6846 | 6769.6374 | 9.7857
204 | 4.166 | 0 | 0 | 130.4783 | 121.2716 | 101944.1515 | 20 | 20.8881 | 22.4508 | 23.6023 | 52.9654 | 48.618 | 4.8 | 20 | 0.30877 | 90.8389 | 6551.6959 | 9.2067
206 | 4.0327 | 0 | 0 | 128.0763 | 119.5876 | 101941.3891 | 20 | 20.8901 | 22.4729 | 23.5943 | 53.0567 | 48.67 | 4.8 | 20 | 0.29889 | 89.0628 | 6412.0388 | 8.4887
208 | 4.1789 | 0 | 0 | 127.7113 | 118.9463 | 101938.8777 | 20 | 20.8821 | 22.4699 | 23.5803 | 53.111 | 48.665 | 4.8 | 20 | 0.30972 | 92.583 | 6664.7494 | 8.765
210 | 4.1685 | 0 | 0 | 129.7467 | 122.1679 | 101942.1419 | 20 | 20.863 | 22.4729 | 23.5692 | 53.0417 | 48.706 | 4.8 | 20 | 0.30895 | 93.6388 | 6726.203 | 7.5788
212 | 4.1014 | 0 | 0 | 130.1982 | 124.8506 | 101934.1081 | 20 | 20.8771 | 22.4729 | 23.5833 | 53.0618 | 48.693 | 4.8 | 20 | 0.30398 | 91.3256 | 6566.4274 | 5.3476
214 | 4.1858 | 0 | 0 | 131.8048 | 126.0413 | 101938.3759 | 20 | 20.866 | 22.4588 | 23.5772 | 53.1642 | 48.735 | 4.8 | 20 | 0.31023 | 93.0296 | 6676.2135 | 5.7635
216 | 4.166 | 0 | 0 | 130.3196 | 120.8496 | 101940.1323 | 20 | 20.863 | 22.498 | 23.5722 | 53.2666 | 48.769 | 4.8 | 20 | 0.30877 | 95.0429 | 6811.651 | 9.47
218 | 4.1794 | 0 | 0 | 129.3232 | 117.7373 | 101935.6136 | 20 | 20.86 | 22.4729 | 23.5752 | 53.2023 | 48.725 | 4.8 | 20 | 0.30976 | 94.0585 | 6751.0135 | 11.5859
220 | 4.1754 | 0 | 0 | 127.5451 | 119.6885 | 101941.891 | 20 | 20.8741 | 22.4619 | 23.5883 | 53.1923 | 48.748 | 4.8 | 20 | 0.30946 | 92.5065 | 6637.49 | 7.8566
222 | 4.1394 | 0 | 0 | 126.8871 | 120.4558 | 101942.6437 | 20 | 20.86 | 22.4649 | 23.5863 | 53.1642 | 48.672 | 4.8 | 20 | 0.30679 | 92.6944 | 6665.7847 | 6.4313
224 | 4.1394 | 0 | 0 | 129.7042 | 122.9753 | 101942.3928 | 20 | 20.8489 | 22.4428 | 23.5662 | 53.2204 | 48.756 | 4.8 | 20 | 0.30679 | 92.0564 | 6597.3575 | 6.7288
226 | 4.1132 | 0 | 0 | 132.226 | 124.2875 | 101939.6305 | 20 | 20.8771 | 22.4839 | 23.5772 | 53.1672 | 48.657 | 4.8 | 20 | 0.30485 | 92.2237 | 6639.5892 | 7.9385
228 | 4.2194 | 0 | 0 | 132.9849 | 123.6386 | 101938.125 | 20 | 20.8851 | 22.4729 | 23.5722 | 53.1822 | 48.714 | 4.8 | 20 | 0.31272 | 93.4799 | 6718.1898 | 9.3463
230 | 4.1468 | 0 | 0 | 127.0768 | 119.0009 | 101941.6401 | 20 | 20.871 | 22.4729 | 23.5973 | 53.2073 | 48.657 | 4.8 | 20 | 0.30734 | 92.6858 | 6671.412 | 8.0759
232 | 4.1547 | 0 | 0 | 127.3614 | 118.7171 | 101940.3832 | 20 | 20.866 | 22.4679 | 23.5833 | 53.1822 | 48.587 | 4.8 | 20 | 0.30793 | 92.8624 | 6699.7957 | 8.6443
234 | 4.1256 | 0 | 0 | 128.1196 | 120.9521 | 101937.8741 | 20 | 20.8791 | 22.4538 | 23.5863 | 53.1411 | 48.6 | 4.8 | 20 | 0.30577 | 90.6501 | 6540.1945 | 7.1675
236 | 4.095 | 0 | 0 | 130.7036 | 122.2088 | 101944.9042 | 20 | 20.852 | 22.4619 | 23.5913 | 53.1692 | 48.576 | 4.8 | 20 | 0.3035 | 91.9865 | 6635.8628 | 8.4948
238 | 4.1562 | 0 | 0 | 129.8878 | 123.7373 | 101938.8777 | 20 | 20.866 | 22.4789 | 23.5863 | 53.1873 | 48.573 | 4.8 | 20 | 0.30804 | 93.5362 | 6751.8176 | 6.1506
240 | 4.0801 | 0 | 0 | 132.0112 | 123.8906 | 101933.8572 | 20 | 20.8791 | 22.4679 | 23.5913 | 53.1973 | 48.555 | 4.8 | 25 | 0.3024 | 72.3621 | 6536.5592 | 8.1207
242 | 4.1512 | 0 | 0 | 130.7659 | 122.391 | 101938.125 | 20 | 20.8821 | 22.5121 | 23.5772 | 53.6089 | 53.363 | 4.8 | 25 | 0.30767 | 75.5311 | 5813.5042 | 8.3749
244 | 4.171 | 0 | 0 | 128.537 | 116.7045 | 101938.3759 | 20 | 20.857 | 22.7049 | 23.7068 | 55.2434 | 55.062 | 4.8 | 25 | 0.30913 | 86.0385 | 6288.4436 | 11.8325
246 | 4.1809 | 0 | 0 | 127.8145 | 118.7998 | 101931.8476 | 20 | 20.868 | 22.7953 | 23.8614 | 56.7575 | 55.648 | 4.8 | 25 | 0.30987 | 89.9452 | 6465.3011 | 9.0147
248 | 4.091 | 0 | 0 | 127.4328 | 120.9923 | 101935.1118 | 20 | 20.871 | 22.8566 | 23.9056 | 58.0115 | 55.988 | 4.8 | 25 | 0.30321 | 90.6725 | 6455.0382 | 6.4404
250 | 4.1656 | 0 | 0 | 127.3607 | 121.8453 | 101939.1286 | 20 | 20.871 | 22.8897 | 23.9558 | 59.1761 | 56.156 | 4.8 | 25 | 0.30873 | 93.8659 | 6650.5643 | 5.5154
252 | 4.1147 | 0 | 0 | 131.0717 | 124.1767 | 101942.8946 | 20 | 20.866 | 22.8837 | 23.9909 | 60.0215 | 56.324 | 4.8 | 25 | 0.30496 | 92.674 | 6534.0729 | 6.895
254 | 4.1438 | 0 | 0 | 133.3393 | 123.9247 | 101935.1118 | 20 | 20.8962 | 22.9199 | 23.9799 | 60.6811 | 56.329 | 4.8 | 25 | 0.30712 | 93.6085 | 6604.6407 | 9.4146
256 | 4.1512 | 0 | 0 | 128.5188 | 120.2175 | 101946.1588 | 20 | 20.871 | 22.9058 | 24.005 | 61.0436 | 56.352 | 4.8 | 25 | 0.30767 | 94.288 | 6643.5613 | 8.3013
258 | 4.1532 | 0 | 0 | 126.8568 | 118.0697 | 101936.6172 | 20 | 20.8791 | 22.8978 | 24.0191 | 61.2815 | 56.423 | 4.8 | 25 | 0.30782 | 93.5877 | 6582.5407 | 8.787
260 | 4.0984 | 0 | 0 | 125.6842 | 120.2645 | 101939.6305 | 20 | 20.8931 | 22.9199 | 23.997 | 61.6409 | 56.423 | 4.8 | 25 | 0.30376 | 92.7204 | 6524.1203 | 5.4197
262 | 4.1384 | 0 | 0 | 127.3007 | 120.3419 | 101937.6232 | 20 | 20.863 | 22.9148 | 24.0271 | 61.9391 | 56.423 | 4.8 | 25 | 0.30672 | 94.7853 | 6663.7585 | 6.9588
264 | 4.0856 | 0 | 0 | 132.1926 | 122.8767 | 101937.8741 | 20 | 20.8881 | 22.9118 | 24.0301 | 61.8839 | 56.36 | 4.8 | 25 | 0.3028 | 92.2926 | 6504.6288 | 9.316
266 | 4.0984 | 0 | 0 | 132.8574 | 124.7474 | 101938.8777 | 20 | 20.8901 | 22.9279 | 24.0572 | 61.662 | 56.365 | 4.8 | 25 | 0.30376 | 93.2259 | 6569.8553 | 8.1101
268 | 4.1522 | 0 | 0 | 131.3533 | 123.0543 | 101932.6004 | 20 | 20.8901 | 22.9671 | 24.0462 | 61.5646 | 56.388 | 4.8 | 25 | 0.30774 | 96.2655 | 6779.6661 | 8.299
270 | 4.1794 | 0 | 0 | 126.2868 | 116.9048 | 101938.3759 | 20 | 20.8881 | 22.9259 | 24.0442 | 61.7182 | 56.431 | 4.8 | 25 | 0.30976 | 95.0676 | 6686.8238 | 9.382
272 | 4.1206 | 0 | 0 | 126.6587 | 118.4507 | 101936.1154 | 20 | 20.9183 | 22.9339 | 24.0492 | 61.8196 | 56.515 | 4.8 | 25 | 0.3054 | 92.7146 | 6511.4532 | 8.208
274 | 4.1557 | 0 | 0 | 128.0581 | 119.3485 | 101930.5931 | 20 | 20.8791 | 22.9339 | 24.0381 | 61.8508 | 56.629 | 4.8 | 25 | 0.308 | 95.3207 | 6665.8012 | 8.7096
276 | 4.1512 | 0 | 0 | 129.6063 | 123.0118 | 101939.8814 | 20 | 20.8881 | 22.9359 | 24.0522 | 62.0496 | 56.685 | 4.8 | 25 | 0.30767 | 94.8929 | 6627.1744 | 6.5945
278 | 4.0895 | 0 | 0 | 131.0975 | 125.2945 | 101936.1154 | 20 | 20.9042 | 22.95 | 24.0492 | 62.1821 | 56.825 | 4.8 | 25 | 0.3031 | 93.3904 | 6499.7416 | 5.803
280 | 4.0722 | 0 | 0 | 131.7502 | 122.5974 | 101931.3458 | 20 | 20.8931 | 22.9691 | 24.0492 | 62.2443 | 56.851 | 4.8 | 25 | 0.30182 | 94.3656 | 6560.8493 | 9.1528
282 | 4.1522 | 0 | 0 | 127.325 | 118.1957 | 101930.3422 | 20 | 20.9042 | 22.947 | 24.0442 | 62.2745 | 56.815 | 4.8 | 25 | 0.30774 | 94.6825 | 6591.5066 | 9.1293
284 | 4.0446 | 0 | 0 | 128.6516 | 116.9564 | 101939.1286 | 20 | 20.9012 | 22.961 | 24.0542 | 62.3518 | 56.874 | 4.8 | 25 | 0.29977 | 92.9994 | 6463.1686 | 11.6951
286 | 4.1009 | 0 | 0 | 128.477 | 122.2422 | 101933.1022 | 20 | 20.9042 | 22.958 | 24.0542 | 62.5144 | 56.963 | 4.8 | 25 | 0.30394 | 94.0175 | 6518.3484 | 6.2348
288 | 4.1256 | 0 | 0 | 128.1393 | 122.0001 | 101935.6136 | 20 | 20.9263 | 22.9721 | 24.0763 | 62.6218 | 57.024 | 4.8 | 25 | 0.30577 | 94.2132 | 6524.8743 | 6.1392
290 | 4.1261 | 0 | 0 | 130.7021 | 124.7709 | 101930.3422 | 20 | 20.9233 | 22.9691 | 24.0572 | 62.6961 | 57.011 | 4.8 | 25 | 0.3058 | 94.2245 | 6527.4666 | 5.9312
292 | 4.1488 | 0 | 0 | 132.0317 | 122.1087 | 101930.5931 | 20 | 20.9424 | 22.9831 | 24.0763 | 62.7393 | 57.042 | 4.8 | 25 | 0.30749 | 94.5104 | 6545.1061 | 9.9231
294 | 4.245 | 0 | 0 | 130.8957 | 121.3695 | 101935.1118 | 20 | 20.9484 | 22.9942 | 24.0853 | 62.8889 | 57.006 | 4.8 | 25 | 0.31462 | 96.9414 | 6721.2841 | 9.5262
296 | 4.1394 | 0 | 0 | 126.3445 | 117.3359 | 101932.0985 | 20 | 20.9233 | 22.9912 | 24.0984 | 62.8518 | 56.97 | 4.8 | 25 | 0.30679 | 95.5499 | 6626.8106 | 9.0086
298 | 4.1646 | 0 | 0 | 126.6883 | 119.1876 | 101932.0985 | 20 | 20.9313 | 22.9691 | 24.0823 | 62.8568 | 57.059 | 4.8 | 25 | 0.30866 | 94.7303 | 6555.2427 | 7.5007
300 | 4.0456 | 0 | 0 | 128.2835 | 122.6429 | 101933.1022 | 20 | 20.9514 | 22.9942 | 24.0964 | 62.916 | 57.133 | 4.8 | 30 | 0.29984 | 76.8754 | 6374.1346 | 5.6406
302 | 4.0866 | 0 | 0 | 130.992 | 123.7107 | 101935.6136 | 20 | 20.9263 | 23.0354 | 24.1124 | 63.4511 | 61.375 | 4.8 | 30 | 0.30288 | 80.1742 | 5946.36 | 7.2813
304 | 4.1784 | 0 | 0 | 132.8377 | 123.7631 | 101928.8344 | 20 | 20.9534 | 23.1961 | 24.2199 | 64.7905 | 62.881 | 4.8 | 30 | 0.30968 | 87.1678 | 6237.0243 | 9.0746
306 | 4.1231 | 0 | 0 | 130.3257 | 121.8112 | 101928.5835 | 20 | 20.9755 | 23.3276 | 24.3855 | 65.914 | 63.336 | 4.8 | 30 | 0.30559 | 90.2131 | 6388.9569 | 8.5145
308 | 4.1364 | 0 | 0 | 125.9149 | 117.8474 | 101929.8403 | 20 | 20.9484 | 23.3528 | 24.4157 | 66.9732 | 63.505 | 4.8 | 30 | 0.30657 | 92.5145 | 6521.7528 | 8.0676
310 | 4.1646 | 0 | 0 | 126.1851 | 117.6303 | 101934.359 | 20 | 20.9645 | 23.3588 | 24.4598 | 67.8226 | 63.622 | 4.8 | 30 | 0.30866 | 92.7547 | 6523.2155 | 8.5548
312 | 4.1537 | 0 | 0 | 128.603 | 121.283 | 101934.359 | 20 | 20.9625 | 23.3889 | 24.488 | 68.6468 | 63.804 | 4.8 | 30 | 0.30785 | 93.7548 | 6565.2239 | 7.32
314 | 4.166 | 0 | 0 | 130.1352 | 122.2278 | 101935.1118 | 20 | 20.9625 | 23.414 | 24.5181 | 69.2322 | 64.038 | 4.8 | 30 | 0.30877 | 95.0064 | 6616.7284 | 7.9074
316 | 4.1734 | 0 | 0 | 130.6718 | 123.203 | 101930.844 | 20 | 20.9755 | 23.4 | 24.5181 | 69.7091 | 64.174 | 4.8 | 30 | 0.30932 | 94.1223 | 6536.5041 | 7.4688
318 | 4.2179 | 0 | 0 | 130.3356 | 123.9847 | 101930.0912 | 20 | 20.9816 | 23.4271 | 24.5151 | 69.8486 | 64.145 | 4.8 | 30 | 0.31261 | 95.9519 | 6668.9716 | 6.3509
320 | 4.0456 | 0 | 0 | 128.8314 | 120.795 | 101933.3554 | 20 | 20.9755 | 23.419 | 24.5372 | 69.9982 | 64.048 | 4.8 | 30 | 0.29984 | 91.9569 | 6404.7996 | 8.0364
322 | 4.0737 | 0 | 0 | 126.746 | 116.495 | 101934.6099 | 20 | 20.9956 | 23.4361 | 24.5452 | 70.1539 | 64.105 | 4.8 | 30 | 0.30193 | 92.4821 | 6435.8681 | 10.2509
324 | 4.0969 | 0 | 0 | 127.0935 | 117.688 | 101930.844 | 20 | 20.9785 | 23.4221 | 24.5181 | 70.451 | 64.232 | 4.8 | 30 | 0.30365 | 93.1238 | 6458.9405 | 9.4055
326 | 4.0732 | 0 | 0 | 130.7234 | 123.3024 | 101931.8476 | 20 | 21.0037 | 23.4442 | 24.5482 | 70.441 | 64.227 | 4.8 | 30 | 0.30189 | 92.4709 | 6418.1204 | 7.421
328 | 4.0856 | 0 | 0 | 131.3153 | 126.3866 | 101934.1081 | 20 | 21.0067 | 23.4552 | 24.5623 | 70.5032 | 64.204 | 4.8 | 30 | 0.3028 | 93.0564 | 6462.6465 | 4.9287
330 | 4.1112 | 0 | 0 | 130.8091 | 122.6171 | 101932.8513 | 20 | 20.9956 | 23.4663 | 24.5542 | 70.6358 | 64.267 | 4.8 | 30 | 0.30471 | 94.4863 | 6550.7254 | 8.192
332 | 4.1512 | 0 | 0 | 130.9617 | 121.4112 | 101927.8307 | 20 | 21.0067 | 23.4823 | 24.6034 | 70.6609 | 64.227 | 4.8 | 30 | 0.30767 | 95.5991 | 6635.705 | 9.5505
334 | 4.1389 | 0 | 0 | 128.8337 | 118.5023 | 101931.0949 | 20 | 21.0227 | 23.4663 | 24.5783 | 70.6257 | 64.267 | 4.8 | 30 | 0.30676 | 94.0774 | 6526.4656 | 10.3314
336 | 4.0994 | 0 | 0 | 126.6989 | 119.004 | 101932.3495 | 20 | 21.0117 | 23.4713 | 24.6064 | 70.4781 | 64.326 | 4.8 | 30 | 0.30383 | 93.7925 | 6496.1779 | 7.6949
338 | 4.1256 | 0 | 0 | 126.538 | 120.348 | 101937.6232 | 20 | 21.0258 | 23.4904 | 24.5864 | 70.3587 | 64.359 | 4.8 | 30 | 0.30577 | 94.5838 | 6548.1225 | 6.19
340 | 4.0717 | 0 | 0 | 129.4067 | 121.8104 | 101930.844 | 20 | 21.0177 | 23.5014 | 24.5924 | 70.5705 | 64.321 | 4.8 | 30 | 0.30178 | 94.0729 | 6517.2614 | 7.5963
342 | 4.1818 | 0 | 0 | 132.6002 | 123.7471 | 101931.8476 | 20 | 21.0589 | 23.5104 | 24.5894 | 70.6559 | 64.331 | 4.8 | 30 | 0.30994 | 95.3659 | 6611.599 | 8.853
344 | 4.0727 | 0 | 0 | 133.2437 | 123.6174 | 101933.1022 | 20 | 21.0288 | 23.5215 | 24.6085 | 70.8004 | 64.346 | 4.8 | 30 | 0.30185 | 94.4381 | 6540.4555 | 9.6263
346 | 4.0752 | 0 | 0 | 129.5767 | 121.9242 | 101932.8513 | 20 | 21.0479 | 23.5104 | 24.6115 | 70.8105 | 64.416 | 4.8 | 30 | 0.30204 | 93.3531 | 6457.7157 | 7.6524
348 | 4.0984 | 0 | 0 | 127.4525 | 117.263 | 101925.5703 | 20 | 21.0308 | 23.5185 | 24.6326 | 70.8406 | 64.483 | 4.8 | 30 | 0.30376 | 94.842 | 6548.0213 | 10.1895
350 | 4.1423 | 0 | 0 | 127.2461 | 118.346 | 101932.8513 | 20 | 21.0479 | 23.5647 | 24.6305 | 71.0354 | 64.456 | 4.8 | 30 | 0.30701 | 96.981 | 6702.4987 | 8.9001
352 | 4.0841 | 0 | 0 | 127.2248 | 120.0057 | 101925.0684 | 20 | 21.0589 | 23.5486 | 24.6275 | 71.0856 | 64.376 | 4.8 | 30 | 0.30269 | 94.5868 | 6550.7695 | 7.2191
354 | 4.2011 | 0 | 0 | 129.5592 | 123.7722 | 101927.5798 | 20 | 21.073 | 23.5295 | 24.6466 | 71.2352 | 64.326 | 4.8 | 30 | 0.31137 | 96.0012 | 6658.5782 | 5.787
356 | 4.1122 | 0 | 0 | 130.5458 | 126.0428 | 101931.8476 | 20 | 21.0559 | 23.5426 | 24.6466 | 71.2181 | 64.227 | 4.8 | 30 | 0.30478 | 95.1233 | 6610.2055 | 4.503
358 | 4.0895 | 0 | 0 | 132.1881 | 122.0199 | 101930.3422 | 20 | 21.0971 | 23.5647 | 24.6546 | 71.1458 | 64.182 | 4.8 | 30 | 0.3031 | 93.8716 | 6536.2757 | 10.1682
360 | 4.171 | 0 | 0 | 131.524 | 120.3958 | 101934.1081 | 20 | 21.075 | 23.5697 | 24.6597 | 71.183 | 64.344 | 4.8 | 35 | 0.30913 | 82.9662 | 6711.0722 | 11.1282
362 | 4.1596 | 0 | 0 | 125.3617 | 116.7341 | 101935.3627 | 20 | 21.1031 | 23.5908 | 24.6486 | 71.6378 | 68.412 | 4.8 | 35 | 0.30829 | 82.5069 | 6104.0136 | 8.6276
364 | 4.1917 | 0 | 0 | 126.837 | 118.7733 | 101926.8271 | 20 | 21.081 | 23.7575 | 24.7671 | 73.1889 | 70.004 | 4.8 | 35 | 0.31067 | 89.4546 | 6399.6709 | 8.0638
366 | 4.1354 | 0 | 0 | 127.7265 | 122.9214 | 101929.8403 | 20 | 21.1111 | 23.8489 | 24.9197 | 74.5966 | 70.544 | 4.8 | 35 | 0.3065 | 90.2735 | 6391.6475 | 4.805
368 | 4.1443 | 0 | 0 | 129.2374 | 124.1152 | 101932.8513 | 20 | 21.1332 | 23.9082 | 24.9629 | 75.5483 | 70.746 | 4.8 | 35 | 0.30716 | 91.6954 | 6468.7747 | 5.1222
370 | 4.0476 | 0 | 0 | 131.2622 | 122.8539 | 101933.1022 | 20 | 21.1222 | 23.9423 | 25.0031 | 76.4389 | 70.865 | 4.8 | 35 | 0.29999 | 91.0132 | 6403.8623 | 8.4083
372 | 4.1117 | 0 | 0 | 129.8006 | 118.8469 | 101932.8513 | 20 | 21.1363 | 23.9614 | 25.0543 | 77.1166 | 71.017 | 4.8 | 35 | 0.30474 | 92.6208 | 6498.9573 | 10.9537
374 | 4.0456 | 0 | 0 | 127.9185 | 117.392 | 101935.1118 | 20 | 21.1383 | 23.9584 | 25.0593 | 77.6477 | 71.089 | 4.8 | 35 | 0.29984 | 90.9686 | 6374.0858 | 10.5264
376 | 4.094 | 0 | 0 | 126.3028 | 117.386 | 101933.3554 | 20 | 21.1383 | 23.9775 | 25.0894 | 77.9951 | 71.268 | 4.8 | 35 | 0.30343 | 92.6794 | 6470.7702 | 8.9168
378 | 4.0441 | 0 | 0 | 129.3642 | 122.3052 | 101929.5871 | 20 | 21.1473 | 24.0066 | 25.0894 | 78.2672 | 71.288 | 4.8 | 35 | 0.29973 | 92.1983 | 6435.7725 | 7.059
380 | 4.1606 | 0 | 0 | 129.4902 | 125.2346 | 101931.8476 | 20 | 21.1744 | 23.9986 | 25.1055 | 78.6025 | 71.438 | 4.8 | 35 | 0.30837 | 93.6882 | 6523.7838 | 4.2556
382 | 4.1063 | 0 | 0 | 129.4833 | 121.8529 | 101929.5871 | 20 | 21.1805 | 24.0126 | 25.1346 | 78.8615 | 71.467 | 4.8 | 35 | 0.30434 | 92.7284 | 6454.001 | 7.6304
384 | 4.0722 | 0 | 0 | 129.2777 | 121.0606 | 101932.0985 | 20 | 21.1774 | 24.0287 | 25.1266 | 78.9399 | 71.542 | 4.8 | 35 | 0.30182 | 92.5788 | 6433.6091 | 8.2171
386 | 4.1068 | 0 | 0 | 127.4305 | 117.9407 | 101929.8403 | 20 | 21.1915 | 24.0337 | 25.1316 | 79.0744 | 71.482 | 4.8 | 35 | 0.30438 | 93.0683 | 6477.1511 | 9.4898
388 | 4.0584 | 0 | 0 | 126.8203 | 116.9261 | 101928.0817 | 20 | 21.1774 | 24.0237 | 25.1316 | 79.1507 | 71.365 | 4.8 | 35 | 0.30079 | 92.102 | 6423.0501 | 9.8943
390 | 3.9858 | 0 | 0 | 127.8373 | 119.734 | 101928.3326 | 20 | 21.1935 | 24.0418 | 25.1396 | 79.224 | 71.36 | 4.8 | 35 | 0.29541 | 90.5188 | 6315.2864 | 8.1032
392 | 4.1122 | 0 | 0 | 129.1684 | 122.8365 | 101928.3326 | 20 | 21.1825 | 24.0418 | 25.1537 | 79.2601 | 71.343 | 4.8 | 35 | 0.30478 | 93.7514 | 6541.5942 | 6.3319
394 | 4.0737 | 0 | 0 | 132.182 | 124.4901 | 101926.8271 | 20 | 21.2247 | 24.0769 | 25.1617 | 79.5051 | 71.475 | 4.8 | 35 | 0.30193 | 92.6448 | 6452.8257 | 7.6919
396 | 4.1522 | 0 | 0 | 129.2746 | 121.2511 | 101929.3362 | 20 | 21.2156 | 24.0769 | 25.1557 | 79.5172 | 71.495 | 4.8 | 35 | 0.30774 | 94.7293 | 6594.2032 | 8.0235
398 | 4.0061 | 0 | 0 | 127.8395 | 119.0313 | 101930.5931 | 20 | 21.2217 | 24.093 | 25.1878 | 79.7451 | 71.547 | 4.8 | 35 | 0.29691 | 91.7162 | 6378.6251 | 8.8082
400 | 4.1112 | 0 | 0 | 127.2195 | 117.4527 | 101929.5871 | 20 | 21.2468 | 24.1091 | 25.2019 | 79.721 | 71.475 | 4.8 | 35 | 0.30471 | 93.8272 | 6538.0608 | 9.7668
402 | 4.0461 | 0 | 0 | 126.2299 | 118.3968 | 101924.3157 | 20 | 21.2407 | 24.098 | 25.2039 | 79.8425 | 71.373 | 4.8 | 35 | 0.29988 | 92.1779 | 6435.4323 | 7.8331
404 | 4.1068 | 0 | 0 | 129.4826 | 121.3088 | 101929.5871 | 20 | 21.2488 | 24.1091 | 25.2099 | 79.733 | 71.37 | 4.8 | 35 | 0.30438 | 93.6599 | 6540.3385 | 8.1738
406 | 4.0717 | 0 | 0 | 130.0533 | 124.2632 | 101933.8572 | 20 | 21.2548 | 24.1121 | 25.2069 | 79.7079 | 71.43 | 4.8 | 35 | 0.30178 | 92.7627 | 6470.7147 | 5.7901
408 | 4.0979 | 0 | 0 | 131.3229 | 123.2364 | 101925.5703 | 20 | 21.2488 | 24.1362 | 25.231 | 79.5955 | 71.555 | 4.8 | 35 | 0.30372 | 94.3434 | 6563.8373 | 8.0865
410 | 4.1779 | 0 | 0 | 128.2099 | 120.9407 | 101929.3362 | 20 | 21.29 | 24.1462 | 25.2451 | 79.6768 | 71.604 | 4.8 | 35 | 0.30965 | 95.1472 | 6618.7365 | 7.2692
412 | 4.1241 | 0 | 0 | 127.7439 | 116.0556 | 101933.1022 | 20 | 21.2769 | 24.1412 | 25.239 | 79.721 | 71.629 | 4.8 | 35 | 0.30566 | 94.186 | 6546.9174 | 11.6883
414 | 4.1384 | 0 | 0 | 126.856 | 117.9711 | 101929.8403 | 20 | 21.2659 | 24.1623 | 25.2581 | 79.74 | 71.579 | 4.8 | 35 | 0.30672 | 95.5735 | 6648.5087 | 8.8849
416 | 4.0717 | 0 | 0 | 128.307 | 120.8777 | 101928.5835 | 20 | 21.2849 | 24.1523 | 25.2692 | 79.8163 | 71.507 | 4.8 | 35 | 0.30178 | 93.0886 | 6487.3881 | 7.4293
418 | 4.0846 | 0 | 0 | 130.6194 | 124.2397 | 101931.0949 | 20 | 21.307 | 24.1603 | 25.2581 | 79.9188 | 71.423 | 4.8 | 35 | 0.30273 | 92.9239 | 6489.6237 | 6.3797
420 | 4.0969 | 0 | 0 | 131.1362 | 124.1175 | 101929.3362 | 20 | 21.3101 | 24.1764 | 25.2611 | 79.8645 | 71.472 | 4.8 | 40 | 0.30365 | 81.9273 | 6533.0276 | 7.0187
422 | 4.0722 | 0 | 0 | 130.1542 | 121.4325 | 101927.5798 | 20 | 21.3231 | 24.2165 | 25.2712 | 80.239 | 75.497 | 4.8 | 40 | 0.30182 | 82.2041 | 6069.6503 | 8.7217
424 | 4.0915 | 0 | 0 | 125.3276 | 117.8914 | 101931.3458 | 20 | 21.3342 | 24.3672 | 25.3896 | 81.5533 | 77.023 | 4.8 | 40 | 0.30324 | 86.5779 | 6218.6929 | 7.4362
426 | 4.0722 | 0 | 0 | 124.0662 | 116.8251 | 101932.6004 | 20 | 21.3372 | 24.4817 | 25.5262 | 82.5031 | 77.428 | 4.8 | 40 | 0.30182 | 89.338 | 6370.9517 | 7.2411
428 | 4.1112 | 0 | 0 | 125.3473 | 119.6293 | 101925.3193 | 20 | 21.3432 | 24.5229 | 25.5744 | 83.4599 | 77.591 | 4.8 | 40 | 0.30471 | 91.2019 | 6485.7233 | 5.718
430 | 4.0959 | 0 | 0 | 127.7082 | 124.3201 | 101927.078 | 20 | 21.3764 | 24.56 | 25.6095 | 84.1938 | 77.888 | 4.8 | 40 | 0.30357 | 90.977 | 6439.5201 | 3.3881
432 | 4.0989 | 0 | 0 | 130.0555 | 122.3978 | 101926.8271 | 20 | 21.3673 | 24.549 | 25.6547 | 85.0994 | 77.973 | 4.8 | 40 | 0.30379 | 90.9854 | 6429.4169 | 7.6577
434 | 4.0851 | 0 | 0 | 130.1648 | 120.1021 | 101919.797 | 20 | 21.3653 | 24.5841 | 25.6628 | 85.8333 | 78.054 | 4.8 | 40 | 0.30277 | 91.7377 | 6473.0866 | 10.0627
436 | 4.054 | 0 | 0 | 129.3353 | 119.3128 | 101927.3289 | 20 | 21.3764 | 24.6032 | 25.7009 | 86.009 | 78.171 | 4.8 | 40 | 0.30046 | 91.2665 | 6427.823 | 10.0225
438 | 4.017 | 0 | 0 | 128.6189 | 117.1249 | 101926.0721 | 20 | 21.3844 | 24.6083 | 25.6959 | 86.3403 | 78.31 | 4.8 | 40 | 0.29772 | 90.3484 | 6348.5247 | 11.494
440 | 3.9898 | 0 | 0 | 125.8747 | 117.8481 | 101925.5703 | 20 | 21.3844 | 24.6163 | 25.7039 | 86.5773 | 78.383 | 4.8 | 40 | 0.29571 | 89.9613 | 6313.2287 | 8.0266
442 | 4.0323 | 0 | 0 | 126.9911 | 119.8767 | 101925.5703 | 20 | 21.4065 | 24.6354 | 25.712 | 86.7219 | 78.373 | 4.8 | 40 | 0.29885 | 90.8337 | 6378.0452 | 7.1144
444 | 4.0895 | 0 | 0 | 130.8835 | 124.7641 | 101931.0949 | 20 | 21.4256 | 24.6293 | 25.725 | 86.7068 | 78.534 | 4.8 | 40 | 0.3031 | 91.4073 | 6402.3677 | 6.1194
446 | 4.0426 | 0 | 0 | 130.517 | 124.5098 | 101926.5762 | 20 | 21.4427 | 24.6645 | 25.7381 | 86.8875 | 78.627 | 4.8 | 40 | 0.29962 | 90.8688 | 6356.2021 | 6.0071
448 | 4.0717 | 0 | 0 | 125.5492 | 118.1699 | 101924.5666 | 20 | 21.4336 | 24.6595 | 25.7702 | 87.01 | 78.541 | 4.8 | 40 | 0.30178 | 91.6377 | 6418.6212 | 7.3792
450 | 3.9671 | 0 | 0 | 125.367 | 117.691 | 101931.5967 | 20 | 21.4447 | 24.6886 | 25.7812 | 87.0431 | 78.444 | 4.8 | 40 | 0.29402 | 89.7825 | 6300.6039 | 7.676
452 | 4.0994 | 0 | 0 | 126.5145 | 118.3581 | 101926.5762 | 20 | 21.4638 | 24.6886 | 25.7812 | 86.9427 | 78.422 | 4.8 | 40 | 0.30383 | 92.231 | 6477.0933 | 8.1564
454 | 4.0056 | 0 | 0 | 126.5646 | 121.8301 | 101927.3289 | 20 | 21.4336 | 24.6836 | 25.7762 | 86.7962 | 78.383 | 4.8 | 40 | 0.29688 | 90.8225 | 6379.1734 | 4.7344
456 | 3.9913 | 0 | 0 | 129.9372 | 123.7373 | 101925.0684 | 20 | 21.4638 | 24.6705 | 25.8023 | 86.7068 | 78.307 | 4.8 | 40 | 0.29582 | 89.295 | 6283.5976 | 6.1999
458 | 4.0174 | 0 | 0 | 132.522 | 122.4957 | 101930.844 | 20 | 21.4808 | 24.7127 | 25.8184 | 86.6446 | 78.31 | 4.8 | 40 | 0.29775 | 90.5841 | 6375.8907 | 10.0263
460 | 4.0974 | 0 | 0 | 131.4034 | 121.031 | 101925.5703 | 20 | 21.4889 | 24.7288 | 25.8023 | 86.6927 | 78.283 | 4.8 | 40 | 0.30368 | 92.6172 | 6523.0096 | 10.3724
462 | 4.095 | 0 | 0 | 126.9478 | 117.9035 | 101926.3253 | 20 | 21.4919 | 24.7157 | 25.8184 | 86.7219 | 78.3 | 4.8 | 40 | 0.3035 | 92.1022 | 6485.1413 | 9.0443
464 | 4.0174 | 0 | 0 | 125.7252 | 116.9883 | 101931.5967 | 20 | 21.522 | 24.7398 | 25.8184 | 86.9156 | 78.344 | 4.8 | 40 | 0.29775 | 90.1898 | 6348.9367 | 8.7369
466 | 4.0219 | 0 | 0 | 126.7057 | 121.5175 | 101925.0684 | 20 | 21.522 | 24.7348 | 25.8345 | 86.9257 | 78.383 | 4.8 | 40 | 0.29808 | 90.1486 | 6341.6848 | 5.1883
468 | 3.9696 | 0 | 0 | 127.0412 | 122.6839 | 101930.0912 | 20 | 21.525 | 24.7589 | 25.8375 | 86.9759 | 78.473 | 4.8 | 40 | 0.29421 | 89.5598 | 6290.6397 | 4.3573
470 | 4.0125 | 0 | 0 | 129.8453 | 124.2647 | 101927.3289 | 20 | 21.5361 | 24.7669 | 25.8455 | 87.007 | 78.495 | 4.8 | 40 | 0.29739 | 90.4444 | 6351.5511 | 5.5806
472 | 4.0456 | 0 | 0 | 129.1585 | 122.5602 | 101922.5593 | 20 | 21.5632 | 24.772 | 25.8807 | 86.8966 | 78.451 | 4.8 | 40 | 0.29984 | 90.5662 | 6368.0589 | 6.5983
474 | 4.0451 | 0 | 0 | 128.9119 | 120.4922 | 101920.5497 | 20 | 21.5502 | 24.783 | 25.8857 | 86.9377 | 78.383 | 4.8 | 40 | 0.2998 | 91.2355 | 6421.3184 | 8.4197
476 | 4.0036 | 0 | 0 | 125.5158 | 116.8745 | 101924.8175 | 20 | 21.5883 | 24.8021 | 25.8837 | 87.1877 | 78.356 | 4.8 | 40 | 0.29673 | 89.7669 | 6325.2106 | 8.6413
478 | 4.0323 | 0 | 0 | 126.8932 | 116.2893 | 101928.0817 | 20 | 21.5944 | 24.8232 | 25.9078 | 87.4608 | 78.354 | 4.8 | 40 | 0.29885 | 90.8327 | 6401.2158 | 10.6038
480 | 4.0189 | 0 | 0 | 128.6736 | 121.481 | 101920.5497 | 20 | 21.6104 | 24.8121 | 25.9238 | 87.4106 | 78.359 | 4.8 | 0 | 0.29786 | Inf | 6327.7016 | 7.1925
482 | 4.0481 | 0 | 0 | 131.2501 | 126.4291 | 101920.5497 | 20 | 21.5913 | 24.6273 | 25.9158 | 84.7882 | 47.636 | 4.8 | 0 | 0.30002 | Inf | 6327.7016 | 4.8209
484 | 3.9459 | 0 | 0 | 131.8253 | 124.6495 | 101919.2952 | 20 | 21.6024 | 23.3889 | 25.1938 | 74.7903 | 33.939 | 4.8 | 0 | 0.29245 | Inf | 6327.7016 | 7.1758
486 | 3.9641 | 0 | 0 | 130.3083 | 122.8342 | 101925.0684 | 20 | 21.6104 | 22.501 | 24.0873 | 64.6298 | 29.473 | 4.8 | 0 | 0.2938 | Inf | 6327.7016 | 7.4741
488 | 3.9641 | 0 | 0 | 130.3083 | 122.8342 | 101925.0684 | 20 | 21.6104 | 22.501 | 24.0873 | 64.6298 | 29.473 | 4.8 | 0 | 0.2938 | Inf | 6327.7016 | 7.4741
490 | 4.0313 | 0 | 0 | 128.5635 | 118.6739 | 101919.0443 | 20 | 21.6486 | 21.9376 | 23.2138 | 49.1763 | 26.553 | 4.8 | 0 | 0.29878 | Inf | 6628.0489 | 9.8897
492 | 4.0046 | 0 | 0 | 127.7606 | 120.8777 | 101922.3061 | 20 | 21.6376 | 21.8693 | 23.0923 | 43.4856 | 25.778 | 4.8 | 0 | 0.2968 | Inf | 6253.8619 | 6.8829

## Heat load scenario 2
Time [s] | Flow rate (left axis) | APExch[kPa] | APAmb[kPa] | Pump (left axis) | AP device (right axis) | Pabs | T Bath [ºC] | T_inlet [ºC] | T_outlet [ºC] | Tin_Exch [ºC] | T_Heater_outside [ºC] | T_Heater (left axis) | V Pump (V) | Power density (right axis) | Re [-] | Energy balance (left axis) | h (left axis) | Rth (left axis) | AP circuit (right axis)
2 | 0.11234 | 0 | 0 | 102.9792 | 13.2745 | 101984.8244 | 20 | 21.1202 | 30.5262 | 26.456 | 56.7816 | 56.882 | 4.2 | 10 | 0.008326 | 29.4873 | 824.5471 | 0.0012128 | 89.7047
4 | 0.072347 | 0 | 0 | 100.084 | 16.9309 | 101981.5602 | 20 | 21.1091 | 30.7923 | 26.7191 | 57.0065 | 57.07 | 4.2 | 10 | 0.005362 | 19.55 | 543.6457 | 0.0018394 | 83.1531
6 | 0.097526 | 0 | 0 | 97.4703 | 13.4309 | 101983.3166 | 20 | 21.1734 | 30.9993 | 26.9932 | 57.2585 | 57.228 | 4.2 | 10 | 0.007228 | 26.7422 | 741.7151 | 0.0013482 | 84.0395
8 | 0.11085 | 0 | 0 | 105.0063 | 19.6501 | 101981.5602 | 20 | 21.1785 | 31.0444 | 27.2884 | 57.4884 | 57.342 | 4.2 | 10 | 0.008216 | 30.5209 | 843.9675 | 0.0011849 | 85.3562
10 | 0.08617 | 0 | 0 | 99.4959 | 14.6132 | 101983.0657 | 20 | 21.1754 | 31.3207 | 27.4681 | 57.6952 | 57.457 | 4.2 | 10 | 0.006387 | 24.3964 | 672.4173 | 0.0014872 | 84.8826
12 | 0.099005 | 0 | 0 | 98.3279 | 13.5758 | 101985.0753 | 20 | 21.1513 | 31.5256 | 27.8547 | 57.8739 | 57.602 | 4.2 | 10 | 0.007338 | 28.663 | 786.3516 | 0.0012717 | 84.7521
14 | 0.11283 | 0 | 0 | 103.3086 | 21.9579 | 101982.062 | 20 | 21.1865 | 31.5225 | 27.9049 | 58.0406 | 57.724 | 4.2 | 10 | 0.008362 | 32.5448 | 890.7227 | 0.0011227 | 81.3507
16 | 0.14838 | 0 | 0 | 99.228 | 12.2561 | 101980.0547 | 20 | 21.1835 | 31.6943 | 28.1168 | 58.15 | 57.838 | 4.2 | 10 | 0.010997 | 43.522 | 1187.3576 | 0.00084221 | 86.9719
18 | 0.074814 | 0 | 0 | 102.0352 | 13.1903 | 101982.8148 | 20 | 21.2227 | 31.8389 | 28.418 | 58.0787 | 57.893 | 4.2 | 10 | 0.005545 | 22.1647 | 604.4302 | 0.0016545 | 88.8449
20 | 0.070867 | 0 | 0 | 102.7842 | 18.256 | 101981.0584 | 20 | 21.1995 | 31.8821 | 28.5937 | 58.0848 | 57.946 | 4.2 | 10 | 0.005252 | 21.1266 | 574.9301 | 0.0017393 | 84.5282
22 | 0.085678 | 0 | 0 | 99.4723 | 13.5189 | 101984.3225 | 20 | 21.1995 | 31.9785 | 28.8237 | 58.2253 | 58.043 | 4.2 | 10 | 0.00635 | 25.7725 | 699.5142 | 0.0014296 | 85.9534
24 | 0.08617 | 0 | 0 | 102.9367 | 14.3734 | 101982.062 | 20 | 21.2427 | 32.1453 | 28.9632 | 58.2966 | 58.122 | 4.2 | 10 | 0.006387 | 26.2175 | 710.8997 | 0.0014067 | 88.5633
26 | 0.071855 | 0 | 0 | 100.7223 | 17.7642 | 101986.0789 | 20 | 21.2598 | 32.2065 | 29.1721 | 58.3498 | 58.197 | 4.2 | 10 | 0.005326 | 21.9508 | 594.2728 | 0.0016827 | 82.958
28 | 0.071855 | 0 | 0 | 98.1351 | 13.298 | 101981.5602 | 20 | 21.2448 | 32.301 | 29.2574 | 58.4904 | 58.278 | 4.2 | 10 | 0.005326 | 22.1703 | 598.6593 | 0.0016704 | 84.8371
30 | 0.077777 | 0 | 0 | 104.9069 | 18.8047 | 101977.2924 | 20 | 21.2478 | 32.3361 | 29.4643 | 58.6089 | 58.338 | 4.2 | 10 | 0.005764 | 24.0671 | 648.8805 | 0.0015411 | 86.1022
32 | 0.060003 | 0 | 0 | 99.8609 | 12.7501 | 101986.3298 | 20 | 21.2709 | 32.5018 | 29.5858 | 58.7213 | 58.381 | 4.2 | 10 | 0.004447 | 18.806 | 506.7622 | 0.0019733 | 87.1108
34 | 0.098018 | 0 | 0 | 97.6472 | 13.3163 | 101983.0657 | 20 | 21.293 | 32.6495 | 29.6671 | 58.7494 | 58.45 | 4.2 | 10 | 0.007265 | 31.064 | 836.0186 | 0.0011961 | 84.3309
36 | 0.084194 | 0 | 0 | 103.8027 | 22.0763 | 101978.7979 | 20 | 21.301 | 32.7047 | 29.8268 | 58.8458 | 58.534 | 4.2 | 10 | 0.00624 | 26.794 | 719.631 | 0.0013896 | 81.7263 | 1
38 | 0.060003 | 0 | 0 | 99.0466 | 13.4339 | 101976.5397 | 20 | 21.2648 | 32.7258 | 29.9764 | 58.8277 | 58.6 | 4.2 | 10 | 0.004447 | 19.1912 | 514.0237 | 0.0019454 | 85.6127
40 | 0.053094 | 0 | 0 | 100.0149 | 13.4574 | 101985.3262 | 20 | 21.304 | 32.8252 | 30.1923 | 58.8408 | 58.58 | 4.2 | 10 | 0.003935 | 17.0706 | 457.9511 | 0.0021836 | 86.5575
42 | 0.21898 | 0 | 0 | 122.5014 | 18.2696 | 101987.3358 | 20 | 21.8134 | 37.1663 | 35.1405 | 76.7552 | 73.007 | 4.5816 | 20 | 0.01623 | 46.9099 | 1832.6468 | 0.00054566 | 104.2317
44 | 0.24218 | 0 | 0 | 124.4973 | 17.5297 | 101989.8449 | 20 | 21.8134 | 37.2607 | 35.2318 | 76.5865 | 75.867 | 4.5816 | 20 | 0.017949 | 52.1989 | 1931.3723 | 0.00051777 | 106.9676
46 | 0.23033 | 0 | 0 | 120.5138 | 15.7015 | 101985.828 | 20 | 21.8495 | 36.651 | 35.5531 | 77.3234 | 77.359 | 4.5816 | 20 | 0.017071 | 47.5696 | 1713.9255 | 0.00058346 | 104.8123
48 | 0.24316 | 0 | 0 | 124.8821 | 23.1289 | 101991.6036 | 20 | 21.8445 | 36.1679 | 35.8996 | 78.2381 | 78.402 | 4.677 | 20 | 0.018022 | 48.5983 | 1718.5456 | 0.00058189 | 101.7532
50 | 0.27032 | 0 | 0 | 124.1444 | 16.7055 | 101992.3563 | 20 | 21.8777 | 36.2643 | 36.0442 | 78.9971 | 79.114 | 5.0745 | 20 | 0.020035 | 54.2641 | 1896.1407 | 0.00052739 | 107.4389
52 | 0.30981 | 0 | 0 | 156.143 | 24.6005 | 101993.3599 | 20 | 21.8797 | 36.5305 | 36.3343 | 79.5864 | 79.357 | 5.3925 | 20 | 0.022962 | 63.3341 | 2203.7946 | 0.00045376 | 131.5425
54 | 0.30981 | 0 | 0 | 167.2496 | 17.938 | 101991.8545 | 20 | 21.9158 | 36.9041 | 36.4679 | 80.2129 | 79.075 | 5.3925 | 20 | 0.022962 | 64.793 | 2267.107 | 0.00044109 | 149.3116
56 | 0.30932 | 0 | 0 | 165.7022 | 19.0581 | 101986.5807 | 20 | 21.944 | 37.0246 | 36.2962 | 80.3575 | 78.743 | 5.3925 | 20 | 0.022925 | 65.089 | 2291.9037 | 0.00043632 | 146.6441
58 | 0.31031 | 0 | 0 | 171.649 | 16.4893 | 101988.0885 | 20 | 21.96 | 36.7083 | 36.3183 | 80.5513 | 78.404 | 5.3289 | 20 | 0.022999 | 63.8573 | 2262.6796 | 0.00044195 | 155.1597
60 | 0.32314 | 0 | 0 | 167.96 | 22.0171 | 101990.8508 | 20 | 21.963 | 36.6008 | 36.4518 | 80.5513 | 78.085 | 5.3289 | 20 | 0.02395 | 66.0005 | 2352.039 | 0.00042516 | 145.9428
62 | 0.28266 | 0 | 0 | 167.1039 | 22.6834 | 101989.8449 | 20 | 21.957 | 36.4913 | 36.6486 | 80.1125 | 77.876 | 5.2017 | 20 | 0.02095 | 57.3243 | 2050.2619 | 0.00048774 | 144.4204
64 | 0.32166 | 0 | 0 | 160.0271 | 22.3184 | 101988.8412 | 20 | 22.0012 | 36.4411 | 36.7631 | 79.9931 | 77.81 | 5.2017 | 20 | 0.02384 | 64.8103 | 2322.5829 | 0.00043056 | 137.7087
66 | 0.32265 | 0 | 0 | 157.1911 | 22.3829 | 101991.6036 | 20 | 22.0233 | 36.3939 | 36.7289 | 79.9097 | 77.824 | 5.2017 | 20 | 0.023913 | 64.6963 | 2318.8367 | 0.00043125 | 134.8081
68 | 0.28118 | 0 | 0 | 157.2814 | 22.3298 | 101992.8581 | 20 | 22.0293 | 36.423 | 36.6988 | 79.9469 | 77.878 | 5.0586 | 20 | 0.02084 | 56.4716 | 2022.3092 | 0.00049448 | 134.9516
70 | 0.28167 | 0 | 0 | 150.7684 | 17.0721 | 101998.6337 | 20 | 22.0565 | 36.4622 | 36.6265 | 79.8806 | 77.902 | 5.0586 | 20 | 0.020876 | 56.6186 | 2027.6864 | 0.00049317 | 133.6963
72 | 0.29994 | 0 | 0 | 150.9892 | 18.6886 | 101992.6072 | 20 | 22.0565 | 36.4883 | 36.5944 | 79.8435 | 77.985 | 5.0586 | 20 | 0.02223 | 60.3994 | 2159.8783 | 0.00046299 | 132.3007
74 | 0.25946 | 0 | 0 | 149.8365 | 20.541 | 101991.8545 | 20 | 22.0675 | 36.5305 | 36.6456 | 79.7431 | 78.105 | 5.0586 | 20 | 0.01923 | 52.3602 | 1868.7574 | 0.00053511 | 129.2954
76 | 0.26933 | 0 | 0 | 151.547 | 20.5927 | 101995.8714 | 20 | 22.0926 | 36.6791 | 36.6587 | 79.8635 | 78.19 | 4.9791 | 20 | 0.019962 | 54.8168 | 1954.3448 | 0.00051168 | 130.9544
78 | 0.26983 | 0 | 0 | 148.2928 | 16.9818 | 101991.6036 | 20 | 22.1117 | 36.7263 | 36.6988 | 79.8977 | 78.317 | 4.9791 | 20 | 0.019998 | 55.0236 | 1957.9526 | 0.00051074 | 131.3111
80 | 0.27032 | 0 | 0 | 146.1398 | 16.1257 | 101990.5976 | 20 | 22.1258 | 36.7896 | 36.7018 | 80.1838 | 78.387 | 4.9791 | 20 | 0.020035 | 55.3095 | 1966.1682 | 0.0005086 | 130.0141
82 | 0.84152 | 0 | 0 | 129.3907 | 28.1066 | 101998.6337 | 20 | 21.3231 | 28.0835 | 26.9932 | 78.6005 | 78.107 | 5.154 | 30 | 0.06237 | 52.9201 | 2795.8664 | 0.00035767 | 101.2841
84 | 0.94421 | 0 | 0 | 153.2948 | 25.2987 | 101988.8412 | 20 | 21.2839 | 29.1622 | 27.6027 | 80.0422 | 79.138 | 5.6787 | 30 | 0.06998 | 69.1965 | 3588.1599 | 0.00027869 | 127.9962
86 | 1.0094 | 0 | 0 | 190.7052 | 31.4944 | 101996.6241 | 20 | 21.2819 | 29.5037 | 28.7273 | 81.3123 | 79.099 | 5.8377 | 30 | 0.074811 | 77.1978 | 4005.625 | 0.00024965 | 159.2108
88 | 1.0765 | 0 | 0 | 197.5824 | 27.3614 | 101989.8449 | 20 | 21.2789 | 29.3962 | 29.5988 | 82.3344 | 78.899 | 6.1238 | 30 | 0.079787 | 81.2868 | 4232.2092 | 0.00023628 | 170.221
90 | 1.1214 | 0 | 0 | 214.1979 | 37.171 | 101994.1127 | 20 | 21.3502 | 29.3179 | 29.9051 | 83 | 78.473 | 6.1238 | 30 | 0.083117 | 83.1179 | 4365.2264 | 0.00022908 | 177.027
92 | 1.1377 | 0 | 0 | 214.0985 | 31.8389 | 102000.8919 | 20 | 21.295 | 29.122 | 29.9613 | 83.5562 | 78.158 | 5.9331 | 30 | 0.084324 | 82.8372 | 4370.3564 | 0.00022881 | 182.2596
94 | 1.1037 | 0 | 0 | 201.9772 | 34.4723 | 101991.3526 | 20 | 21.2869 | 29.0929 | 29.9452 | 83.6145 | 78.351 | 5.9331 | 30 | 0.081799 | 80.1405 | 4213.1877 | 0.00023735 | 167.5049
96 | 1.0903 | 0 | 0 | 201.9028 | 30.4205 | 101992.6072 | 20 | 21.3141 | 29.1863 | 29.884 | 84.0211 | 78.417 | 5.5356 | 30 | 0.080811 | 79.8448 | 4194.7821 | 0.00023839 | 171.4823
98 | 1.1052 | 0 | 0 | 202.5699 | 34.6742 | 101995.8714 | 20 | 21.3472 | 29.2436 | 29.9051 | 84.2289 | 78.426 | 5.5356 | 30 | 0.081909 | 81.1771 | 4266.5831 | 0.00023438 | 167.8958
100 | 1.0114 | 0 | 0 | 176.5902 | 31.5262 | 101993.109 | 20 | 21.3121 | 29.2938 | 29.9965 | 84.5693 | 78.897 | 5.5356 | 30 | 0.074957 | 75.0905 | 3911.9867 | 0.00025562 | 145.064
102 | 0.98321 | 0 | 0 | 175.4838 | 31.3373 | 101991.8545 | 20 | 21.298 | 29.5007 | 30.0396 | 84.992 | 79.248 | 5.5356 | 30 | 0.072871 | 75.022 | 3883.7962 | 0.00025748 | 144.1465
104 | 0.98321 | 0 | 0 | 177.913 | 29.4863 | 102000.8919 | 20 | 21.3312 | 29.6724 | 30.1441 | 85.1827 | 79.448 | 5.5356 | 30 | 0.072871 | 76.2896 | 3938.0822 | 0.00025393 | 148.4267
106 | 0.95359 | 0 | 0 | 176.4635 | 30.1496 | 101994.8677 | 20 | 21.3533 | 29.7588 | 30.2997 | 85.4739 | 79.601 | 5.5356 | 30 | 0.070676 | 74.5614 | 3840.2202 | 0.0002604 | 146.3139
108 | 0.95704 | 0 | 0 | 178.4746 | 30.2877 | 101994.1127 | 20 | 21.3281 | 29.8583 | 30.4363 | 85.4859 | 79.64 | 5.5356 | 30 | 0.070932 | 75.9403 | 3906.9412 | 0.00025595 | 148.1869
110 | 0.95655 | 0 | 0 | 178.4025 | 32.1546 | 101997.3768 | 20 | 21.3643 | 29.9065 | 30.5487 | 85.4106 | 79.769 | 5.7 | 30 | 0.070895 | 76.0085 | 3904.233 | 0.00025613 | 146.2479
112 | 1.0025 | 0 | 0 | 176.2518 | 33.164 | 101996.1223 | 20 | 21.3563 | 29.9145 | 30.6351 | 85.6516 | 79.823 | 5.7 | 30 | 0.074298 | 79.8066 | 4094.9742 | 0.0002442 | 143.0878
114 | 1.0671 | 0 | 0 | 190.7272 | 28.505 | 101996.1223 | 20 | 21.3784 | 29.9567 | 30.6833 | 85.8293 | 79.66 | 5.7 | 30 | 0.079091 | 85.1546 | 4383.2664 | 0.00022814 | 162.2222
116 | 1.0227 | 0 | 0 | 192.4158 | 30.7817 | 101984.8244 | 20 | 21.4226 | 29.8743 | 30.7284 | 86.0552 | 79.509 | 5.7 | 30 | 0.075798 | 80.405 | 4152.6907 | 0.00024081 | 161.634
118 | 1.0513 | 0 | 0 | 190.7044 | 32.2222 | 101985.0753 | 20 | 21.4356 | 29.8281 | 30.7505 | 85.9086 | 79.526 | 5.6 | 30 | 0.07792 | 82.0766 | 4238.7385 | 0.00023592 | 158.4823
120 | 0.98469 | 0 | 0 | 184.5322 | 30.4751 | 101991.1017 | 20 | 21.4226 | 29.8362 | 30.7345 | 85.8434 | 79.477 | 5.6 | 30 | 0.072981 | 77.067 | 3982.4876 | 0.0002511 | 154.0571
122 | 3.9641 | 0 | 0 | 120.3271 | 111.191 | 101990.3467 | 20 | 21.508 | 24.7901 | 25.9068 | 88.0692 | 79.331 | 4.7 | 40 | 0.2938 | 90.7707 | 6279.2069 | 0.00015926 | 9.1361
124 | 3.9676 | 0 | 0 | 122.1819 | 115.7687 | 101990.3467 | 20 | 21.5431 | 24.8142 | 25.9228 | 87.9849 | 79.413 | 4.7 | 40 | 0.29406 | 90.5438 | 6258.4402 | 0.00015978 | 6.4131
126 | 4.0041 | 0 | 0 | 124.8707 | 116.3599 | 101992.1054 | 20 | 21.5381 | 24.8252 | 25.9198 | 87.9969 | 79.44 | 4.7 | 40 | 0.29677 | 91.8265 | 6343.5932 | 0.00015764 | 8.5108
128 | 4.0174 | 0 | 0 | 120.1579 | 111.9848 | 101990.0958 | 20 | 21.5542 | 24.8252 | 25.9278 | 88.1606 | 79.323 | 4.7 | 40 | 0.29775 | 91.6816 | 6348.1738 | 0.00015753 | 8.173
130 | 3.9503 | 0 | 0 | 123.1798 | 117.0642 | 101987.5867 | 20 | 21.5682 | 24.8252 | 25.9529 | 88.513 | 79.365 | 4.7 | 40 | 0.29278 | 89.7618 | 6212.2387 | 0.00016097 | 6.1156
132 | 3.9918 | 0 | 0 | 120.7688 | 110.9246 | 101993.8618 | 20 | 21.5763 | 24.8543 | 25.9529 | 88.5662 | 79.409 | 4.7 | 40 | 0.29585 | 91.2915 | 6314.1748 | 0.00015837 | 9.8442
134 | 4.0273 | 0 | 0 | 120.0068 | 112.6489 | 101986.3298 | 20 | 21.5984 | 24.8704 | 25.955 | 88.5803 | 79.489 | 4.7 | 40 | 0.29849 | 91.9349 | 6352.3177 | 0.00015742 | 7.358
136 | 4.0298 | 0 | 0 | 125.5256 | 117.5727 | 101991.3526 | 20 | 21.6185 | 24.8815 | 25.969 | 88.6475 | 79.548 | 4.7 | 40 | 0.29867 | 91.7371 | 6334.3906 | 0.00015787 | 7.953
138 | 4.0031 | 0 | 0 | 121.7182 | 110.9717 | 101992.6072 | 20 | 21.6094 | 24.8704 | 25.9791 | 88.9136 | 79.518 | 4.7 | 40 | 0.29669 | 91.0741 | 6290.8918 | 0.00015896 | 10.7465
140 | 3.9513 | 0 | 0 | 122.3777 | 114.2707 | 101993.8618 | 20 | 21.6506 | 24.8925 | 25.9931 | 88.8373 | 79.496 | 4.8 | 40 | 0.29285 | 89.3685 | 6179.8182 | 0.00016182 | 8.107
142 | 4.0856 | 0 | 0 | 127.7037 | 117.0908 | 101988.8412 | 20 | 21.6426 | 24.8624 | 25.9851 | 88.8855 | 79.396 | 4.8 | 40 | 0.3028 | 91.7758 | 6356.3886 | 0.00015732 | 10.6129
144 | 4.128 | 0 | 0 | 126.727 | 117.1545 | 101989.3431 | 20 | 21.6506 | 24.8383 | 25.961 | 88.8513 | 79.265 | 4.8 | 40 | 0.30595 | 91.8039 | 6373.6813 | 0.0001569 | 9.5725
146 | 4.0866 | 0 | 0 | 126.6693 | 117.8648 | 101993.109 | 20 | 21.6787 | 24.8624 | 25.958 | 88.777 | 79.15 | 4.8 | 40 | 0.30288 | 90.7669 | 6317.376 | 0.00015829 | 8.8045
148 | 4.1438 | 0 | 0 | 127.1451 | 119.8661 | 101994.8677 | 20 | 21.6818 | 24.8604 | 25.9449 | 88.7218 | 79.167 | 4.8 | 40 | 0.30712 | 91.8937 | 6394.2438 | 0.00015639 | 7.279
150 | 4.1137 | 0 | 0 | 129.0659 | 122.1428 | 101992.1054 | 20 | 21.6838 | 24.8604 | 25.955 | 88.5612 | 79.238 | 4.7 | 40 | 0.30489 | 91.1682 | 6336.1599 | 0.00015782 | 6.9231
152 | 3.8832 | 0 | 0 | 124.7189 | 119.328 | 101985.828 | 20 | 21.7089 | 24.9136 | 25.9951 | 88.5441 | 79.348 | 4.7 | 40 | 0.2878 | 86.8204 | 6025.1018 | 0.00016597 | 5.3909
154 | 3.9631 | 0 | 0 | 119.531 | 113.2302 | 101988.5903 | 20 | 21.731 | 24.9668 | 26.0574 | 88.5943 | 79.423 | 4.7 | 40 | 0.29373 | 89.4694 | 6203.2422 | 0.00016121 | 6.3008
156 | 3.9508 | 0 | 0 | 119.8376 | 113.426 | 101989.3431 | 20 | 21.745 | 24.9889 | 26.0594 | 88.4407 | 79.426 | 4.7 | 40 | 0.29282 | 89.4121 | 6200.4607 | 0.00016128 | 6.4116
158 | 4.0318 | 0 | 0 | 123.9327 | 116.174 | 101991.8545 | 20 | 21.7561 | 25.013 | 26.0865 | 88.4407 | 79.406 | 4.7 | 40 | 0.29882 | 91.6118 | 6356.4207 | 0.00015732 | 7.7587
160 | 4.0402 | 0 | 0 | 120.3529 | 111.9112 | 101991.3526 | 20 | 21.731 | 25.013 | 26.1086 | 88.3092 | 79.431 | 4.7 | 40 | 0.29944 | 92.5104 | 6413.1962 | 0.00015593 | 8.4417
162 | 7.6189 | 0 | 0 | 418.3625 | 388.8368 | 101984.0716 | 20 | 23.5674 | 25.4449 | 26.5484 | 90.0039 | 79.533 | 8.6 | 43 | 0.56468 | 92.8368 | 7132.9169 | 0.0001402 | 29.5257
164 | 7.499 | 0 | 0 | 418.9992 | 383.0448 | 101986.5807 | 20 | 23.5573 | 25.467 | 26.5614 | 90.011 | 79.548 | 8.6 | 43 | 0.55579 | 92.9392 | 7137.596 | 0.0001401 | 35.9544
166 | 7.5651 | 0 | 0 | 421.2418 | 388.4991 | 101981.3093 | 20 | 23.5754 | 25.4319 | 26.5675 | 89.7901 | 79.501 | 8.6 | 43 | 0.56069 | 91.1454 | 7007.9776 | 0.00014269 | 32.7427
168 | 7.5794 | 0 | 0 | 419.6291 | 383.4387 | 101990.8508 | 20 | 23.5915 | 25.4801 | 26.5966 | 89.8784 | 79.491 | 8.6 | 43 | 0.56175 | 92.8987 | 7146.1177 | 0.00013994 | 36.1904
170 | 7.5113 | 0 | 0 | 421.2805 | 391.9195 | 101983.5698 | 20 | 23.5734 | 25.461 | 26.5775 | 90.009 | 79.494 | 8.6 | 43 | 0.55671 | 92.0149 | 7075.4631 | 0.00014133 | 29.361
172 | 7.4733 | 0 | 0 | 420.5717 | 384.6021 | 101992.1054 | 20 | 23.5945 | 25.5333 | 26.6096 | 90.0612 | 79.426 | 8.6 | 43 | 0.55389 | 94.0334 | 7242.2175 | 0.00013808 | 35.9696
174 | 7.5508 | 0 | 0 | 419.5183 | 389.3544 | 101983.0657 | 20 | 23.5915 | 25.469 | 26.5966 | 90.021 | 79.474 | 8.6 | 43 | 0.55963 | 92.0063 | 7079.6259 | 0.00014125 | 30.1639
176 | 7.457 | 0 | 0 | 420.9929 | 385.4407 | 101988.8412 | 20 | 23.6106 | 25.5092 | 26.6157 | 90.013 | 79.423 | 8.6 | 43 | 0.55268 | 91.884 | 7079.0901 | 0.00014126 | 35.5522
178 | 7.5389 | 0 | 0 | 415.5674 | 387.1695 | 101983.0657 | 20 | 23.6478 | 25.5524 | 26.6659 | 89.8784 | 79.431 | 8.6 | 43 | 0.55875 | 93.1883 | 7183.3313 | 0.00013921 | 28.398
180 | 7.4303 | 0 | 0 | 421.4627 | 387.5239 | 101984.0716 | 20 | 23.6156 | 25.5072 | 26.6478 | 89.8694 | 79.47 | 8.6 | 43 | 0.5507 | 91.2164 | 7022.3761 | 0.0001424 | 33.9388
182 | 7.3193 | 0 | 0 | 415.3595 | 389.1707 | 101984.3225 | 20 | 23.6538 | 25.5604 | 26.6769 | 89.8885 | 79.457 | 8.6 | 43 | 0.54247 | 90.568 | 6978.8555 | 0.00014329 | 26.1888
184 | 7.4195 | 0 | 0 | 425.1555 | 384.3441 | 101982.062 | 20 | 23.6618 | 25.5554 | 26.6879 | 89.5622 | 79.606 | 8.6 | 43 | 0.5499 | 91.1793 | 7008.2545 | 0.00014269 | 40.8114
186 | 7.4333 | 0 | 0 | 420.4336 | 390.5018 | 101983.0657 | 20 | 23.6638 | 25.5152 | 26.6608 | 89.4256 | 79.638 | 8.6 | 43 | 0.55092 | 89.3141 | 6861.2124 | 0.00014575 | 29.9317
188 | 7.458 | 0 | 0 | 418.8361 | 380.2171 | 101986.0789 | 20 | 23.6588 | 25.5926 | 26.7171 | 89.6264 | 79.596 | 8.6 | 43 | 0.55275 | 93.5972 | 7194.9973 | 0.00013899 | 38.6189
190 | 7.4165 | 0 | 0 | 419.2527 | 392.0045 | 101982.8148 | 20 | 23.699 | 25.6006 | 26.7201 | 89.8232 | 79.645 | 8.6 | 43 | 0.54968 | 91.5293 | 7034.9294 | 0.00014215 | 27.2482
192 | 7.5064 | 0 | 0 | 421.5241 | 384.7895 | 101986.5807 | 20 | 23.7151 | 25.6117 | 26.709 | 89.8784 | 79.623 | 8.6 | 43 | 0.55634 | 92.3934 | 7106.1751 | 0.00014072 | 36.7346
194 | 7.4052 | 0 | 0 | 419.8302 | 388.5765 | 101983.0657 | 20 | 23.71 | 25.5976 | 26.7231 | 90.03 | 79.64 | 8.6 | 43 | 0.54884 | 90.7133 | 6974.2095 | 0.00014339 | 31.2537
196 | 7.4447 | 0 | 0 | 419.9957 | 385.8171 | 101992.6072 | 20 | 23.7291 | 25.6197 | 26.7472 | 90.2077 | 79.538 | 8.6 | 43 | 0.55176 | 91.3425 | 7037.8205 | 0.00014209 | 34.1786
198 | 7.4308 | 0 | 0 | 417.3008 | 383.8181 | 101984.0716 | 20 | 23.7231 | 25.6117 | 26.7442 | 90.0491 | 79.494 | 8.6 | 43 | 0.55074 | 91.0761 | 7022.0709 | 0.00014241 | 33.4827
200 | 7.4076 | 0 | 0 | 418.3063 | 384.8282 | 101991.6036 | 20 | 23.7211 | 25.6408 | 26.7602 | 89.9869 | 79.487 | 8.6 | 43 | 0.54902 | 92.2886 | 7116.1929 | 0.00014052 | 33.4781
202 | 7.4175 | 0 | 0 | 421.5423 | 385.0498 | 101980.5566 | 20 | 23.699 | 25.6086 | 26.7522 | 89.9557 | 79.511 | 8.6 | 43 | 0.54975 | 91.9283 | 7082.5557 | 0.00014119 | 36.4925
204 | 7.3982 | 0 | 0 | 415.5189 | 382.8551 | 101993.6109 | 20 | 23.7713 | 25.681 | 26.7633 | 90.0401 | 79.645 | 8.5816 | 0 | 0.54833 | Inf | 7056.3219 | 0.00014172 | 32.6638
206 | 7.4279 | 0 | 0 | 423.3379 | 390.2066 | 101986.5807 | 20 | 23.7311 | 25.3917 | 26.712 | 87.5793 | 48.018 | 8.3791 | 0 | 0.55052 | Inf | 14172.6641 | 7.0558e-05 | 33.1313
208 | 7.2729 | 0 | 0 | 404.4176 | 381.0071 | 101996.1223 | 20 | 23.7291 | 24.5892 | 25.958 | 77.1909 | 34.556 | 8.3238 | 0 | 0.53903 | Inf | 16122.3299 | 6.2026e-05 | 23.4104

## Heat load scenario 3
Time [s] | Flow rate (left axis) | APExch[kPa] | APAmb[kPa] | Pump (left axis) | Heater (left axis) | Pabs | T Bath [ºC] | Tin_Dev [ºC] | Tout_Dev [ºC] | Tin_Exch [ºC] | T_Heater_outside [ºC] | T_Heater (left axis) | V Pump (V) | Power density (right axis) | Re [-] | Energy balance (left axis) | h (left axis)
0 | 3.2902 | 0 | 0 | 96.1147 | 94.8996 | 101479.667 | 20 | 21.4316 | 22.5402 | 24.3273 | 63.3287 | 29.138 | 4.2 | 0 | 0.24386 | Inf | 13208.447 | 3.3776 | 79.359 | 6490.0934 | 93.0366
2 | 3.3524 | 0 | 0 | 99.7824 | 92.1 | 101475.3992 | 20 | 21.4396 | 22.1676 | 23.762 | 56.7334 | 27.815 | 4.2 | 0 | 0.24847 | Inf | 10681.8023
4 | 3.3752 | 0 | 0 | 98.8702 | 94.6325 | 101477.6597 | 20 | 21.4728 | 21.9807 | 23.4176 | 49.6301 | 26.76 | 4.2 | 0 | 0.25015 | Inf | 9048.7974
6 | 3.3534 | 0 | 0 | 95.7876 | 92.3953 | 101474.1446 | 20 | 21.511 | 21.9004 | 23.2107 | 43.9073 | 26.003 | 4.2 | 40 | 0.24854 | 9.1107 | 8112.7701
8 | 3.3811 | 0 | 0 | 99.293 | 92.2518 | 101472.6369 | 20 | 21.4698 | 22.1023 | 23.0943 | 43.1533 | 60.228 | 4.2 | 40 | 0.25059 | 14.9196 | 1539.757
10 | 3.4556 | 0 | 0 | 95.7117 | 90.5298 | 101478.1615 | 20 | 21.4587 | 23.5787 | 23.9166 | 50.8921 | 70.991 | 4.2 | 40 | 0.25612 | 51.1107 | 4127.4674
12 | 3.4324 | 0 | 0 | 94.4663 | 89.4583 | 101479.667 | 20 | 21.525 | 24.556 | 25.1687 | 58.7886 | 74.672 | 4.2 | 40 | 0.2544 | 72.5825 | 5462.7798
14 | 3.4324 | 0 | 0 | 99.1503 | 96.5563 | 101474.3955 | 20 | 21.525 | 24.9347 | 25.7833 | 65.2503 | 76.135 | 4.2 | 40 | 0.2544 | 81.6502 | 5980.6098
16 | 3.4196 | 0 | 0 | 95.3163 | 88.7935 | 101474.8974 | 20 | 21.507 | 25.0994 | 26.0855 | 70.4701 | 76.963 | 4.2 | 40 | 0.25344 | 85.7061 | 6181.9127
18 | 3.3944 | 0 | 0 | 95.3626 | 89.2723 | 101477.6597 | 20 | 21.4879 | 25.2059 | 26.2471 | 74.6046 | 77.484 | 4.2 | 40 | 0.25158 | 88.0483 | 6289.6021
20 | 3.3919 | 0 | 0 | 98.55 | 95.9128 | 101477.1556 | 20 | 21.5411 | 25.2892 | 26.3566 | 77.6588 | 77.918 | 4.2 | 40 | 0.25139 | 88.697 | 6293.1493
22 | 3.3677 | 0 | 0 | 94.6613 | 90.3765 | 101473.1387 | 20 | 21.5341 | 25.3184 | 26.4068 | 80.226 | 78.084 | 4.2 | 40 | 0.2496 | 88.9142 | 6289.251
24 | 3.3786 | 0 | 0 | 98.0924 | 89.4074 | 101476.4028 | 20 | 21.5682 | 25.4088 | 26.4871 | 82.2812 | 78.235 | 4.2 | 40 | 0.25041 | 90.5265 | 6390.0972
26 | 3.3668 | 0 | 0 | 93.8417 | 92.6282 | 101480.1688 | 20 | 21.5944 | 25.4278 | 26.5654 | 83.744 | 78.364 | 4.2 | 40 | 0.24953 | 90.0438 | 6344.5045
28 | 3.3934 | 0 | 0 | 92.1114 | 86.6405 | 101483.182 | 20 | 21.6024 | 25.452 | 26.5946 | 84.8594 | 78.581 | 4.2 | 40 | 0.2515 | 91.1372 | 6397.9958
30 | 3.4063 | 0 | 0 | 101.3837 | 96.9882 | 101467.6163 | 20 | 21.6155 | 25.4811 | 26.6086 | 85.9699 | 78.76 | 4.2 | 40 | 0.25246 | 91.8638 | 6430.2748
32 | 3.3653 | 0 | 0 | 95.1994 | 87.9344 | 101477.4065 | 20 | 21.6285 | 25.5012 | 26.6588 | 86.7229 | 78.884 | 4.2 | 40 | 0.24942 | 90.9237 | 6352.1358
34 | 3.3278 | 0 | 0 | 96.2467 | 88.9415 | 101480.4197 | 20 | 21.6526 | 25.5464 | 26.6689 | 87.2751 | 78.962 | 4.2 | 40 | 0.24664 | 90.3996 | 6309.5819
36 | 3.3529 | 0 | 0 | 97.461 | 93.7264 | 101480.1688 | 20 | 21.6325 | 25.5434 | 26.6769 | 87.8965 | 79.04 | 4.2 | 40 | 0.24851 | 91.4831 | 6374.2974 |  |  |  |  | 1
38 | 3.3796 | 0 | 0 | 94.8898 | 89.8628 | 101477.1556 | 20 | 21.5994 | 25.5142 | 26.6398 | 88.3112 | 79.189 | 4.2 | 40 | 0.25048 | 92.3053 | 6411.2469
40 | 3.3929 | 0 | 0 | 100.1672 | 91.8549 | 101474.1446 | 20 | 21.6245 | 25.5574 | 26.6719 | 88.5833 | 79.34 | 4.2 | 40 | 0.25147 | 93.0972 | 6452.1417
42 | 3.3529 | 0 | 0 | 95.9424 | 93.1048 | 101484.9407 | 20 | 21.6325 | 25.5926 | 26.701 | 88.7148 | 79.377 | 4.2 | 40 | 0.24851 | 92.6343 | 6416.8456
44 | 3.3406 | 0 | 0 | 93.7886 | 89.9591 | 101478.6633 | 20 | 21.6134 | 25.5604 | 26.7171 | 89.1515 | 79.464 | 4.2 | 40 | 0.24759 | 91.9891 | 6360.4627
46 | 3.3653 | 0 | 0 | 100.2788 | 95.8369 | 101472.3859 | 20 | 21.6104 | 25.5494 | 26.7231 | 89.3513 | 79.589 | 4.2 | 40 | 0.24942 | 92.4801 | 6380.2976
48 | 3.4186 | 0 | 0 | 94.6249 | 88.4193 | 101477.6597 | 20 | 21.6245 | 25.5624 | 26.701 | 89.3895 | 79.635 | 4.2 | 40 | 0.25337 | 93.9214 | 6476.167 | [5 empty] | 1
50 | 3.3909 | 0 | 0 | 95.3899 | 88.2607 | 101478.9142 | 20 | 21.6496 | 25.6247 | 26.7361 | 89.4708 | 79.647 | 4.2 | 40 | 0.25132 | 94.0409 | 6485.8743
52 | 3.3672 | 0 | 0 | 99.3757 | 96.5214 | 101479.667 | 20 | 21.6054 | 25.5926 | 26.7251 | 89.5572 | 79.629 | 4.2 | 40 | 0.24957 | 93.667 | 6457.1684
54 | 3.4438 | 0 | 0 | 94.8435 | 90.0419 | 101473.6405 | 20 | 21.6195 | 25.5906 | 26.7331 | 89.519 | 79.548 | 4.2 | 40 | 0.25524 | 95.4094 | 6588.0802
56 | 3.3796 | 0 | 0 | 94.7251 | 91.713 | 101484.9407 | 20 | 21.6335 | 25.5986 | 26.7402 | 89.6867 | 79.634 | 4.2 | 40 | 0.25048 | 93.4893 | 6447.4836
58 | 3.348 | 0 | 0 | 97.9831 | 92.9402 | 101483.6839 | 20 | 21.6818 | 25.6438 | 26.7693 | 90.0401 | 79.781 | 4.2 | 40 | 0.24814 | 92.5446 | 6371.4833
60 | 3.4206 | 0 | 0 | 94.5293 | 89.2587 | 101479.9179 | 20 | 21.6737 | 25.6368 | 26.7733 | 90.2047 | 79.841 | 4.2 | 40 | 0.25352 | 94.5747 | 6503.6355
62 | 3.3539 | 0 | 0 | 99.7604 | 93.5526 | 101476.6537 | 20 | 21.6396 | 25.6096 | 26.7803 | 90.3845 | 79.884 | 4.2 | 40 | 0.24858 | 92.8966 | 6379.7758
64 | 3.3949 | 0 | 0 | 94.8503 | 91.9445 | 101484.6875 | 20 | 21.6607 | 25.5936 | 26.7703 | 90.3855 | 79.968 | 4.2 | 40 | 0.25161 | 93.1512 | 6390.3574
66 | 3.3663 | 0 | 0 | 94.8291 | 89.8688 | 101485.4425 | 20 | 21.7008 | 25.6669 | 26.7984 | 90.6897 | 80.04 | 4.2 | 40 | 0.24949 | 93.1437 | 6386.3622
68 | 3.4196 | 0 | 0 | 100.0116 | 95.9401 | 101481.6766 | 20 | 21.6908 | 25.681 | 26.8135 | 90.6144 | 80.007 | 4.2 | 40 | 0.25344 | 95.1943 | 6529.526
70 | 3.3663 | 0 | 0 | 94.0314 | 88.6166 | 101481.9275 | 20 | 21.6707 | 25.692 | 26.8165 | 90.4357 | 79.99 | 4.2 | 40 | 0.24949 | 94.4413 | 6477.5311
72 | 3.3776 | 0 | 0 | 94.5756 | 87.8031 | 101489.2085 | 20 | 21.6717 | 25.6699 | 26.8356 | 90.4437 | 79.843 | 4.2 | 40 | 0.25033 | 94.2155 | 6478.4872
74 | 3.4462 | 0 | 0 | 95.0408 | 92.9834 | 101487.1989 | 20 | 21.6998 | 25.7 | 26.8145 | 90.3764 | 79.777 | 4.2 | 40 | 0.25542 | 96.1779 | 6624.1433
76 | 3.4063 | 0 | 0 | 94.3722 | 90.8069 | 101479.9179 | 20 | 21.735 | 25.7161 | 26.8466 | 90.4176 | 79.777 | 4.2 | 40 | 0.25246 | 94.6081 | 6519.9777
78 | 3.3929 | 0 | 0 | 100.089 | 93.6277 | 101481.6766 | 20 | 21.7049 | 25.7081 | 26.8596 | 90.3041 | 79.725 | 4.2 | 40 | 0.25147 | 94.7611 | 6532.977
80 | 3.4082 | 0 | 0 | 93.7476 | 90.0032 | 101482.6802 | 20 | 21.7079 | 25.697 | 26.8466 | 90.3784 | 79.757 | 4.2 | 40 | 0.2526 | 94.8542 | 6536.1326
82 | 3.3811 | 0 | 0 | 95.4157 | 89.3991 | 101485.9443 | 20 | 21.7189 | 25.692 | 26.8516 | 90.4869 | 79.747 | 4.2 | 40 | 0.25059 | 93.7193 | 6460.2745
84 | 3.4196 | 0 | 0 | 98.6433 | 97.0648 | 101486.1953 | 20 | 21.6998 | 25.6759 | 26.8576 | 90.5511 | 79.711 | 4.2 | 40 | 0.25344 | 94.8588 | 6540.7258
86 | 3.3381 | 0 | 0 | 94.5983 | 89.9197 | 101481.6766 | 20 | 21.7129 | 25.6689 | 26.8335 | 90.5491 | 79.758 | 4.2 | 40 | 0.24741 | 92.1312 | 6348.9393
88 | 3.3786 | 0 | 0 | 99.0099 | 89.3664 | 101488.4557 | 20 | 21.738 | 25.7513 | 26.8837 | 90.4919 | 79.854 | 4.2 | 40 | 0.25041 | 94.5979 | 6510.9696
90 | 3.3663 | 0 | 0 | 95.5569 | 92.1008 | 101488.9576 | 20 | 21.7712 | 25.7061 | 26.8767 | 90.2369 | 79.744 | 4.2 | 40 | 0.24949 | 92.4122 | 6376.2396
92 | 3.3534 | 0 | 0 | 93.3515 | 89.4507 | 101486.948 | 20 | 21.7139 | 25.7141 | 26.8737 | 90.1073 | 79.765 | 4.2 | 40 | 0.24854 | 93.5875 | 6448.6283
94 | 3.3574 | 0 | 0 | 100.0526 | 96.6095 | 101484.4366 | 20 | 21.7511 | 25.7272 | 26.8526 | 90.1154 | 79.707 | 4.2 | 40 | 0.24883 | 93.1329 | 6427.8457
96 | 3.389 | 0 | 0 | 94.8336 | 88.452 | 101485.6934 | 20 | 21.7802 | 25.7593 | 26.8978 | 90.1425 | 79.807 | 4.2 | 40 | 0.25118 | 94.0805 | 6485.3172
98 | 3.384 | 0 | 0 | 95.4301 | 89.2868 | 101488.2026 | 20 | 21.733 | 25.7703 | 26.9219 | 89.9045 | 79.741 | 4.2 | 40 | 0.25081 | 95.319 | 6572.8186
100 | 3.3544 | 0 | 0 | 98.4999 | 96.5275 | 101482.9311 | 20 | 21.744 | 25.7302 | 26.8848 | 89.768 | 79.663 | 4.2 | 40 | 0.24861 | 93.2858 | 6442.5075
102 | 3.4457 | 0 | 0 | 94.4033 | 89.6723 | 101480.9215 | 20 | 21.7471 | 25.7171 | 26.8807 | 89.5873 | 79.663 | 4.2 | 40 | 0.25538 | 95.4394 | 6591.5817
104 | 3.383 | 0 | 0 | 93.4084 | 90.2407 | 101489.9612 | 20 | 21.7852 | 25.7673 | 26.8948 | 89.3875 | 79.64 | 4.2 | 40 | 0.25074 | 93.9871 | 6498.1415
106 | 3.3648 | 0 | 0 | 99.3514 | 95.3869 | 101490.2121 | 20 | 21.8033 | 25.7774 | 26.946 | 89.3232 | 79.641 | 4.2 | 40 | 0.24938 | 93.291 | 6451.9151
108 | 3.4028 | 0 | 0 | 95.2214 | 90.142 | 101486.948 | 20 | 21.7762 | 25.7804 | 26.935 | 89.2861 | 79.576 | 4.2 | 40 | 0.2522 | 95.0604 | 6578.597
110 | 3.4201 | 0 | 0 | 99.2967 | 94.0436 | 101480.6706 | 20 | 21.7872 | 25.7593 | 26.9239 | 89.4919 | 79.607 | 4.2 | 40 | 0.25348 | 94.7761 | 6556.6604
112 | 3.4072 | 0 | 0 | 94.1863 | 91.099 | 101487.4498 | 20 | 21.8324 | 25.7754 | 26.9249 | 89.3162 | 79.555 | 4.2 | 40 | 0.25253 | 93.7278 | 6495.0577
114 | 3.3796 | 0 | 0 | 94.5794 | 90.3894 | 101491.2158 | 20 | 21.8405 | 25.8045 | 26.957 | 89.529 | 79.555 | 4.2 | 40 | 0.25048 | 93.4646 | 6477.7192
116 | 3.3129 | 0 | 0 | 100.1467 | 97.2879 | 101483.4329 | 20 | 21.7963 | 25.8025 | 26.957 | 89.52 | 79.526 | 4.2 | 40 | 0.24554 | 92.5966 | 6415.8726
118 | 3.4087 | 0 | 0 | 95.8581 | 89.2875 | 101487.7007 | 20 | 21.8134 | 25.7834 | 26.942 | 89.5833 | 79.524 | 4.2 | 40 | 0.25264 | 94.4135 | 6543.9258
120 | 3.3465 | 0 | 0 | 94.4708 | 89.267 | 101493.4763 | 20 | 21.8606 | 25.8417 | 26.955 | 89.53 | 79.44 | 4.2 | 40 | 0.24803 | 92.9484 | 6457.0582
122 | 3.3806 | 0 | 0 | 98.5432 | 95.8673 | 101490.9649 | 20 | 21.8706 | 25.8517 | 26.9651 | 89.6786 | 79.524 | 4.2 | 40 | 0.25055 | 93.8945 | 6514.414
124 | 3.3786 | 0 | 0 | 95.0484 | 91.0254 | 101483.6839 | 20 | 21.8576 | 25.8336 | 26.9992 | 89.7459 | 79.556 | 4.2 | 40 | 0.25041 | 93.7213 | 6497.3206
126 | 3.3668 | 0 | 0 | 98.1273 | 90.9359 | 101488.4557 | 20 | 21.8324 | 25.8296 | 26.9872 | 89.9236 | 79.698 | 4.2 | 40 | 0.24953 | 93.8882 | 6490.0934
128 | 3.3524 | 0 | 0 | 95.7496 | 92.2336 | 101491.7176 | 20 | 21.8686 | 25.8457 | 26.9892 | 90.1013 | 79.78 | 4.2 | 40 | 0.24847 | 93.0189 | 6424.9118
130 | 3.4058 | 0 | 0 | 95.0788 | 88.8754 | 101483.9348 | 20 | 21.8967 | 25.8638 | 27.0163 | 90.1234 | 79.778 | 4.2 | 40 | 0.25242 | 94.2596 | 6513.998
132 | 3.3529 | 0 | 0 | 100.8244 | 94.8101 | 101480.6706 | 20 | 21.8746 | 25.8668 | 26.9972 | 90.1114 | 79.617 | 4.2 | 40 | 0.24851 | 93.3851 | 6469.0848
134 | 3.3638 | 0 | 0 | 93.7673 | 91.392 | 101482.6802 | 20 | 21.8415 | 25.8346 | 26.9922 | 90.0441 | 79.6 | 4.2 | 40 | 0.24931 | 93.7113 | 6489.8662
136 | 3.3929 | 0 | 0 | 94.6757 | 90.6232 | 101489.2085 | 20 | 21.8576 | 25.8537 | 26.9892 | 90.0822 | 79.683 | 4.2 | 40 | 0.25147 | 94.5939 | 6543.4114
138 | 3.3979 | 0 | 0 | 100.2856 | 96.5791 | 101488.4557 | 20 | 21.8857 | 25.8828 | 27.0193 | 90.0009 | 79.744 | 4.2 | 40 | 0.25183 | 94.7553 | 6550.8494
140 | 3.3791 | 0 | 0 | 95.9295 | 88.2486 | 101481.1724 | 20 | 21.8545 | 25.8859 | 27.0374 | 90.0973 | 79.778 | 4.2 | 40 | 0.25044 | 95.0373 | 6562.9573
142 | 3.3253 | 0 | 0 | 95.8119 | 90.438 | 101490.714 | 20 | 21.8686 | 25.8859 | 27.0324 | 90.2429 | 79.768 | 4.2 | 40 | 0.24646 | 93.1976 | 6438.5913
144 | 3.4329 | 0 | 0 | 98.8498 | 96.7665 | 101487.1989 | 20 | 21.8686 | 25.8617 | 27.0193 | 90.3081 | 79.78 | 4.2 | 40 | 0.25443 | 95.6366 | 6605.7202
146 | 3.3663 | 0 | 0 | 95.6054 | 90.4896 | 101485.6934 | 20 | 21.8576 | 25.8457 | 27.0052 | 90.2218 | 79.741 | 4.2 | 40 | 0.24949 | 93.662 | 6472.4533
148 | 3.3737 | 0 | 0 | 97.3016 | 90.8524 | 101490.463 | 20 | 21.9188 | 25.91 | 27.0454 | 90.1415 | 79.808 | 4.2 | 40 | 0.25004 | 93.9386 | 6490.9318
150 | 3.3786 | 0 | 0 | 93.737 | 90.9131 | 101488.7067 | 20 | 21.9219 | 25.8909 | 27.0424 | 90.3041 | 79.847 | 4.2 | 40 | 0.25041 | 93.5553 | 6460.4267
152 | 3.3357 | 0 | 0 | 94.1369 | 89.8833 | 101487.7007 | 20 | 21.9118 | 25.8999 | 27.0595 | 90.53 | 79.942 | 4.2 | 40 | 0.24722 | 92.81 | 6397.3628
154 | 3.3011 | 0 | 0 | 101.5014 | 96.9479 | 101480.6706 | 20 | 21.8977 | 25.8889 | 27.0615 | 90.6445 | 79.986 | 4.2 | 40 | 0.24466 | 91.918 | 6329.544
156 | 3.4067 | 0 | 0 | 94.4443 | 88.3958 | 101484.9407 | 20 | 21.951 | 25.9531 | 27.0705 | 90.6535 | 80.063 | 4.2 | 40 | 0.25249 | 95.1221 | 6547.4992
158 | 3.3924 | 0 | 0 | 94.9042 | 89.6351 | 101490.463 | 20 | 21.952 | 25.9722 | 27.1077 | 90.6063 | 79.956 | 4.2 | 40 | 0.25143 | 95.1503 | 6561.6354
160 | 3.3939 | 0 | 0 | 100.4002 | 95.6973 | 101486.6971 | 20 | 21.9379 | 25.9642 | 27.1077 | 90.4236 | 79.961 | 4.2 | 40 | 0.25154 | 95.3345 | 6572.1814
162 | 3.3712 | 0 | 0 | 95.7375 | 89.248 | 101485.4425 | 20 | 21.9188 | 25.926 | 27.0916 | 90.5029 | 79.959 | 4.2 | 40 | 0.24986 | 94.2479 | 6495.3595
164 | 3.4053 | 0 | 0 | 96.2217 | 89.9553 | 101489.7103 | 20 | 21.9882 | 25.9773 | 27.1107 | 90.7017 | 79.966 | 4.2 | 40 | 0.25238 | 94.7704 | 6538.3878
166 | 3.3914 | 0 | 0 | 94.1491 | 94.9437 | 101489.9612 | 20 | 21.9851 | 25.9803 | 27.1157 | 90.9306 | 80.029 | 4.2 | 40 | 0.25136 | 94.5283 | 6514.2676
168 | 3.3924 | 0 | 0 | 93.8281 | 91.3184 | 101495.4836 | 20 | 21.946 | 25.9692 | 27.1157 | 90.7338 | 80.029 | 4.2 | 40 | 0.25143 | 95.2216 | 6557.621
170 | 3.3806 | 0 | 0 | 101.342 | 93.734 | 101481.4256 | 20 | 21.9409 | 25.9642 | 27.1077 | 90.6545 | 80 | 4.2 | 40 | 0.25055 | 94.8891 | 6537.4193
172 | 3.3524 | 0 | 0 | 94.5589 | 89.1577 | 101485.1916 | 20 | 21.946 | 25.9341 | 27.0946 | 90.4859 | 80.044 | 4.2 | 40 | 0.24847 | 93.2769 | 6422.0376
174 | 3.3796 | 0 | 0 | 93.6641 | 89.9432 | 101494.229 | 20 | 21.9771 | 25.9963 | 27.1267 | 90.3443 | 79.891 | 4.2 | 40 | 0.25048 | 94.7665 | 6545.3367
176 | 3.3436 | 0 | 0 | 98.2282 | 97.0253 | 101489.2085 | 20 | 21.9661 | 25.9853 | 27.1187 | 90.025 | 79.659 | 4.2 | 40 | 0.24781 | 93.756 | 6500.3415
178 | 3.3687 | 0 | 0 | 94.5308 | 90.6323 | 101484.1857 | 20 | 21.946 | 25.9421 | 27.1026 | 90.0009 | 79.615 | 4.2 | 40 | 0.24968 | 93.9192 | 6514.3566
180 | 3.4058 | 0 | 0 | 95.3026 | 90.4843 | 101485.9443 | 20 | 21.949 | 25.9341 | 27.0785 | 89.9196 | 79.63 | 4.2 | 40 | 0.25242 | 94.6889 | 6566.384
182 | 3.3944 | 0 | 0 | 97.4352 | 95.1038 | 101490.463 | 20 | 21.9882 | 25.9983 | 27.1267 | 90.0521 | 79.496 | 4.2 | 40 | 0.25158 | 94.9677 | 6605.5453
184 | 3.3658 | 0 | 0 | 95.122 | 90.8198 | 101483.182 | 20 | 21.9841 | 25.9953 | 27.1398 | 89.7439 | 79.503 | 4.2 | 40 | 0.24946 | 94.1902 | 6550.2101
186 | 3.3909 | 0 | 0 | 99.3787 | 92.4507 | 101484.4366 | 20 | 21.9711 | 25.9682 | 27.1478 | 89.5692 | 79.496 | 4.2 | 40 | 0.25132 | 94.5622 | 6575.3896
188 | 3.3579 | 0 | 0 | 95.7367 | 90.6171 | 101488.2026 | 20 | 21.9681 | 25.9602 | 27.1287 | 89.5712 | 79.438 | 4.2 | 40 | 0.24887 | 93.522 | 6509.2848
190 | 3.3579 | 0 | 0 | 94.8549 | 89.3953 | 101487.1989 | 20 | 22.0072 | 25.9722 | 27.1227 | 89.6877 | 79.529 | 4.2 | 40 | 0.24887 | 92.8866 | 6459.2295
192 | 3.4063 | 0 | 0 | 98.355 | 97.8821 | 101486.948 | 20 | 22.0223 | 26.0194 | 27.1538 | 89.8634 | 79.571 | 4.2 | 40 | 0.25246 | 94.9887 | 6602.318
194 | 3.3653 | 0 | 0 | 94.3957 | 89.6396 | 101481.4256 | 20 | 22.0032 | 25.9973 | 27.1549 | 89.9146 | 79.576 | 4.2 | 40 | 0.24942 | 93.7753 | 6515.2528
196 | 3.3796 | 0 | 0 | 97.2204 | 90.0707 | 101487.7007 | 20 | 22.0354 | 26.0094 | 27.1679 | 89.8031 | 79.602 | 4.2 | 40 | 0.25048 | 93.7005 | 6510.7527
198 | 3.3791 | 0 | 0 | 99.1025 | 94.1961 | 101489.2085 | 20 | 22.0364 | 26.0235 | 27.188 | 89.6907 | 79.605 | 4.2 | 40 | 0.25044 | 93.9946 | 6530.9591
200 | 3.383 | 0 | 0 | 94.2978 | 89.4332 | 101484.4366 | 20 | 22.0002 | 25.9943 | 27.1739 | 89.8182 | 79.612 | 4.2 | 40 | 0.25074 | 94.2706 | 6545.2292
202 | 3.3406 | 0 | 0 | 98.0112 | 91.1901 | 101483.182 | 20 | 22.0555 | 26.0506 | 27.1749 | 89.9899 | 79.611 | 4.2 | 40 | 0.24759 | 93.1106 | 6471.0127
204 | 3.3791 | 0 | 0 | 94.4428 | 93.032 | 101491.9708 | 20 | 22.0575 | 26.0687 | 27.191 | 89.8072 | 79.572 | 4.2 | 40 | 0.25044 | 94.5628 | 6576.618
206 | 3.3677 | 0 | 0 | 93.9472 | 89.8673 | 101486.948 | 20 | 22.0374 | 26.0425 | 27.181 | 89.6656 | 79.569 | 4.2 | 40 | 0.2496 | 94.1036 | 6542.7393
208 | 3.3613 | 0 | 0 | 100.7516 | 96.2194 | 101489.7103 | 20 | 22.0324 | 26.0204 | 27.181 | 89.5361 | 79.552 | 4.2 | 40 | 0.24913 | 93.5239 | 6503.7868
210 | 3.3519 | 0 | 0 | 95.1873 | 89.9986 | 101487.4498 | 20 | 22.0655 | 26.0556 | 27.183 | 89.5933 | 79.596 | 4.2 | 40 | 0.24843 | 93.3097 | 6487.6686
212 | 3.426 | 0 | 0 | 95.0196 | 89.0659 | 101488.7067 | 20 | 22.0776 | 26.0556 | 27.201 | 89.7871 | 79.59 | 4.2 | 40 | 0.25392 | 95.083 | 6613.0412
214 | 3.3806 | 0 | 0 | 98.4741 | 96.7711 | 101485.6934 | 20 | 22.0193 | 26.0295 | 27.2101 | 89.8312 | 79.429 | 4.2 | 40 | 0.25055 | 94.5808 | 6589.8814
216 | 3.4344 | 0 | 0 | 94.3851 | 89.7368 | 101484.4366 | 20 | 22.0233 | 26.0164 | 27.179 | 89.6977 | 79.271 | 4.2 | 40 | 0.25454 | 95.6772 | 6685.1412
218 | 3.4058 | 0 | 0 | 96.9237 | 91.9285 | 101487.1989 | 20 | 22.0715 | 26.0536 | 27.198 | 89.8112 | 79.187 | 4.2 | 40 | 0.25242 | 94.6168 | 6626.3501
220 | 3.3914 | 0 | 0 | 97.9482 | 95.6274 | 101487.7007 | 20 | 22.0725 | 26.0496 | 27.189 | 89.6315 | 79.146 | 4.2 | 40 | 0.25136 | 94.1001 | 6595.0182
222 | 3.3944 | 0 | 0 | 93.6436 | 89.9743 | 101489.4594 | 20 | 22.0414 | 26.0476 | 27.196 | 89.4206 | 79.142 | 4.2 | 40 | 0.25158 | 94.8723 | 6645.9738
224 | 3.4196 | 0 | 0 | 100.2006 | 93.4448 | 101488.4557 | 20 | 22.0504 | 26.0194 | 27.186 | 89.3272 | 79.01 | 4.2 | 40 | 0.25344 | 94.6894 | 6649.5866
226 | 3.4324 | 0 | 0 | 93.8129 | 91.0406 | 101494.4799 | 20 | 22.0866 | 26.0385 | 27.1779 | 89.2881 | 78.949 | 4.2 | 40 | 0.2544 | 94.6357 | 6657.1758
228 | 3.3658 | 0 | 0 | 94.694 | 89.0462 | 101491.7176 | 20 | 22.0866 | 26.0516 | 27.2111 | 89.4136 | 78.961 | 4.2 | 40 | 0.24946 | 93.1048 | 6548.097
230 | 3.3776 | 0 | 0 | 99.765 | 96.9753 | 101483.6839 | 20 | 22.0615 | 26.0385 | 27.194 | 89.3272 | 79.007 | 4.2 | 40 | 0.25033 | 93.7166 | 6582.8991
232 | 3.3401 | 0 | 0 | 93.0062 | 89.0211 | 101488.4557 | 20 | 22.0364 | 26.0034 | 27.1699 | 89.4517 | 78.997 | 4.2 | 40 | 0.24755 | 92.4417 | 6491.6206
234 | 3.3529 | 0 | 0 | 93.5086 | 89.5979 | 101493.7272 | 20 | 22.1087 | 26.0435 | 27.192 | 89.4427 | 78.925 | 4.2 | 40 | 0.24851 | 92.0447 | 6480.1655
236 | 3.3796 | 0 | 0 | 98.4126 | 95.9849 | 101488.4557 | 20 | 22.0977 | 26.0405 | 27.189 | 89.3162 | 78.857 | 4.2 | 40 | 0.25048 | 92.9661 | 6551.5969
238 | 3.4067 | 0 | 0 | 94.7175 | 89.8506 | 101490.714 | 20 | 22.0967 | 26.0616 | 27.198 | 89.1385 | 78.866 | 4.2 | 40 | 0.25249 | 94.2381 | 6640.0713
240 | 3.4329 | 0 | 0 | 97.7918 | 89.0644 | 101488.2026 | 20 | 22.0715 | 26.0415 | 27.198 | 89.0903 | 78.869 | 4.2 | 40 | 0.25443 | 95.0824 | 6696.2404
242 | 3.3811 | 0 | 0 | 95.0628 | 91.5043 | 101497.7441 | 20 | 22.0876 | 26.0285 | 27.179 | 88.9337 | 78.865 | 4.2 | 40 | 0.25059 | 92.9594 | 6549.0464
244 | 3.3524 | 0 | 0 | 96.1845 | 88.691 | 101491.2158 | 20 | 22.1288 | 26.0586 | 27.2191 | 89.0983 | 79.059 | 4.2 | 40 | 0.24847 | 91.9136 | 6457.9834
246 | 3.3791 | 0 | 0 | 99.699 | 94.9824 | 101490.2121 | 20 | 22.1328 | 26.0827 | 27.2171 | 89.3192 | 79.115 | 4.2 | 40 | 0.25044 | 93.118 | 6536.6414
248 | 3.3421 | 0 | 0 | 93.4516 | 88.4861 | 101488.9576 | 20 | 22.0926 | 26.0435 | 27.2292 | 89.3252 | 79.115 | 4.2 | 40 | 0.2477 | 92.1213 | 6462.1148
250 | 3.3445 | 0 | 0 | 95.1326 | 90.0973 | 101489.4594 | 20 | 22.1037 | 26.0496 | 27.2101 | 89.4387 | 79.102 | 4.2 | 40 | 0.24788 | 92.0722 | 6461.3952
252 | 3.3213 | 0 | 0 | 98.6919 | 96.6315 | 101493.2254 | 20 | 22.1338 | 26.0777 | 27.2422 | 89.3905 | 79.176 | 4.2 | 40 | 0.24616 | 91.3867 | 6408.3592
254 | 3.3554 | 0 | 0 | 93.9798 | 89.6359 | 101487.9516 | 20 | 22.1298 | 26.0998 | 27.2472 | 89.6064 | 79.149 | 4.2 | 40 | 0.24869 | 92.9353 | 6519.5803
256 | 3.3791 | 0 | 0 | 95.9644 | 90.8122 | 101489.4594 | 20 | 22.1127 | 26.0857 | 27.2261 | 89.7359 | 79.149 | 4.2 | 40 | 0.25044 | 93.6627 | 6568.6425
258 | 3.3391 | 0 | 0 | 98.2305 | 94.4868 | 101496.9913 | 20 | 22.1389 | 26.0707 | 27.2061 | 89.8463 | 79.205 | 4.2 | 40 | 0.24748 | 91.5949 | 6420.2634
260 | 3.3672 | 0 | 0 | 93.633 | 89.1555 | 101484.4366 | 20 | 22.0926 | 26.0415 | 27.2 | 89.8794 | 79.232 | 4.2 | 40 | 0.24957 | 92.7681 | 6494.1655
262 | 3.3544 | 0 | 0 | 99.2201 | 91.5612 | 101488.4557 | 20 | 22.1368 | 26.0958 | 27.2141 | 89.519 | 79.307 | 4.2 | 40 | 0.24861 | 92.6493 | 6482.3573
264 | 3.3411 | 0 | 0 | 93.016 | 89.4112 | 101498.7477 | 20 | 22.1389 | 26.0737 | 27.2352 | 89.5481 | 79.359 | 4.2 | 40 | 0.24763 | 91.7192 | 6411.6734
266 | 3.3791 | 0 | 0 | 94.1901 | 88.395 | 101494.7308 | 20 | 22.1167 | 26.0707 | 27.2352 | 89.6445 | 79.307 | 4.2 | 40 | 0.25044 | 93.2128 | 6519.4891
268 | 3.4058 | 0 | 0 | 99.7369 | 96.1313 | 101493.2254 | 20 | 22.1057 | 26.0536 | 27.2231 | 89.9728 | 79.259 | 4.2 | 40 | 0.25242 | 93.8052 | 6565.1619
270 | 3.3539 | 0 | 0 | 94.0421 | 89.7429 | 101498.7477 | 20 | 22.1378 | 26.0616 | 27.2121 | 89.7549 | 79.181 | 4.2 | 40 | 0.24858 | 91.8132 | 6438.1567
272 | 3.3391 | 0 | 0 | 94.1369 | 90.2528 | 101492.4726 | 20 | 22.1599 | 26.0857 | 27.2392 | 89.9537 | 79.139 | 4.2 | 40 | 0.24748 | 91.4544 | 6420.2148
274 | 3.3658 | 0 | 0 | 98.1796 | 96.0524 | 101496.2386 | 20 | 22.1268 | 26.0586 | 27.2101 | 90.031 | 79.125 | 4.2 | 40 | 0.24946 | 92.3263 | 6479.2395
276 | 3.4467 | 0 | 0 | 94.3456 | 89.7558 | 101493.2254 | 20 | 22.0906 | 26.0536 | 27.196 | 90.1365 | 79.061 | 4.2 | 40 | 0.25546 | 95.2961 | 6690.921
278 | 3.4196 | 0 | 0 | 98.893 | 89.6639 | 101489.9612 | 20 | 22.1439 | 26.0546 | 27.191 | 89.9487 | 79.109 | 4.2 | 40 | 0.25344 | 93.2991 | 6551.3146
280 | 3.3668 | 0 | 0 | 95.8612 | 91.3958 | 101494.4799 | 20 | 22.1489 | 26.0988 | 27.2422 | 89.9698 | 79.092 | 4.2 | 40 | 0.24953 | 92.7779 | 6517.2354
282 | 3.3129 | 0 | 0 | 93.8698 | 87.8714 | 101497.2422 | 20 | 22.165 | 26.0978 | 27.2432 | 89.9296 | 78.956 | 4.2 | 40 | 0.24554 | 90.9002 | 6402.4363
284 | 3.3243 | 0 | 0 | 100.0913 | 93.0335 | 101488.7067 | 20 | 22.1469 | 26.0707 | 27.2302 | 89.8584 | 78.83 | 4.2 | 40 | 0.24638 | 91.0023 | 6421.8251
286 | 3.3924 | 0 | 0 | 92.6487 | 86.9417 | 101493.7272 | 20 | 22.1429 | 26.0506 | 27.2302 | 89.9688 | 78.784 | 4.2 | 40 | 0.25143 | 92.4869 | 6531.4319
288 | 3.3796 | 0 | 0 | 93.3849 | 88.0862 | 101496.4895 | 20 | 22.1971 | 26.0988 | 27.2352 | 90.0481 | 78.818 | 4.2 | 40 | 0.25048 | 91.9946 | 6498.9906
290 | 3.3524 | 0 | 0 | 97.914 | 96.381 | 101494.4799 | 20 | 22.1841 | 26.1118 | 27.2271 | 90.1314 | 78.728 | 4.2 | 40 | 0.24847 | 91.8663 | 6498.7562
292 | 3.3529 | 0 | 0 | 93.0456 | 89.1319 | 101487.4498 | 20 | 22.162 | 26.0797 | 27.2251 | 90.0883 | 78.757 | 4.2 | 40 | 0.24851 | 91.6451 | 6477.2505
294 | 3.4151 | 0 | 0 | 94.1635 | 90.8865 | 101491.7176 | 20 | 22.17 | 26.0586 | 27.2111 | 90.1415 | 78.708 | 4.2 | 40 | 0.25311 | 92.6512 | 6554.9662
296 | 3.3352 | 0 | 0 | 95.931 | 94.269 | 101503.7705 | 20 | 22.1841 | 26.0847 | 27.2332 | 90.2349 | 78.699 | 4.2 | 40 | 0.24719 | 90.7619 | 6423.9191
298 | 3.3001 | 0 | 0 | 94.8655 | 89.5827 | 101492.7235 | 20 | 22.165 | 26.1008 | 27.2412 | 90.1084 | 78.786 | 4.2 | 40 | 0.24459 | 90.6174 | 6401.6804
300 | 3.3791 | 0 | 0 | 99.6246 | 94.8928 | 101492.2217 | 20 | 22.165 | 26.0847 | 27.2251 | 89.8995 | 79.02 | 4.2 | 40 | 0.25044 | 92.4075 | 6501.2722
302 | 3.3124 | 0 | 0 | 95.4643 | 88.4079 | 101501.51 | 20 | 22.1338 | 26.0606 | 27.179 | 89.6686 | 79.059 | 4.2 | 40 | 0.2455 | 90.7475 | 6376.6166
304 | 3.3939 | 0 | 0 | 94.955 | 88.2296 | 101498.2459 | 20 | 22.1841 | 26.1088 | 27.2141 | 89.3855 | 79.132 | 4.2 | 40 | 0.25154 | 92.9314 | 6527.4602
306 | 3.3534 | 0 | 0 | 99.2011 | 96.2285 | 101492.7235 | 20 | 22.1861 | 26.1038 | 27.2573 | 89.4537 | 79.221 | 4.2 | 40 | 0.24854 | 91.6584 | 6428.2283
308 | 3.4161 | 0 | 0 | 94.6188 | 87.8889 | 101491.9708 | 20 | 22.1549 | 26.0958 | 27.2492 | 89.5973 | 79.243 | 4.2 | 40 | 0.25319 | 93.9228 | 6580.9067
310 | 3.4063 | 0 | 0 | 93.8812 | 87.6521 | 101498.2459 | 20 | 22.1519 | 26.1118 | 27.2512 | 89.7389 | 79.227 | 4.2 | 40 | 0.25246 | 94.1049 | 6595.1656
312 | 3.3663 | 0 | 0 | 97.4443 | 95.5068 | 101495.4836 | 20 | 22.1599 | 26.0807 | 27.2482 | 89.9146 | 79.218 | 4.2 | 40 | 0.24949 | 92.0801 | 6455.1877
314 | 3.3855 | 0 | 0 | 93.63 | 89.5182 | 101490.9649 | 20 | 22.1579 | 26.0827 | 27.2583 | 89.9065 | 79.272 | 4.2 | 40 | 0.25092 | 92.7017 | 6492.3879
316 | 3.4186 | 0 | 0 | 99.1662 | 93.5139 | 101493.7272 | 20 | 22.1509 | 26.0907 | 27.2673 | 89.8343 | 79.246 | 4.2 | 40 | 0.25337 | 93.9668 | 6583.1814
318 | 3.3263 | 0 | 0 | 95.3079 | 88.8678 | 101496.7404 | 20 | 22.179 | 26.1179 | 27.2693 | 89.8483 | 79.309 | 4.2 | 40 | 0.24653 | 91.4057 | 6399.842
320 | 3.3796 | 0 | 0 | 94.9831 | 88.8147 | 101502.7669 | 20 | 22.1509 | 26.1018 | 27.2834 | 89.8513 | 79.431 | 4.2 | 40 | 0.25048 | 93.1553 | 6505.2465
322 | 3.3801 | 0 | 0 | 99.5935 | 94.9027 | 101493.2254 | 20 | 22.1861 | 26.1229 | 27.2613 | 89.8935 | 79.479 | 4.2 | 40 | 0.25052 | 92.8371 | 6481.5722
324 | 3.3258 | 0 | 0 | 93.4273 | 87.948 | 101495.9877 | 20 | 22.2142 | 26.142 | 27.3035 | 90.0521 | 79.527 | 4.2 | 40 | 0.24649 | 91.1357 | 6360.5796
326 | 3.3791 | 0 | 0 | 94.5741 | 89.0196 | 101503.2687 | 20 | 22.2132 | 26.155 | 27.3115 | 90.0983 | 79.486 | 4.2 | 40 | 0.25044 | 92.9282 | 6490.2148
328 | 3.3549 | 0 | 0 | 98.6843 | 95.9348 | 101495.9877 | 20 | 22.2011 | 26.153 | 27.3035 | 90.1997 | 79.428 | 4.2 | 40 | 0.24865 | 92.4982 | 6465.3682
330 | 3.4112 | 0 | 0 | 93.2164 | 89.8863 | 101492.2217 | 20 | 22.2011 | 26.1309 | 27.3035 | 90.26 | 79.408 | 4.2 | 40 | 0.25282 | 93.524 | 6539.3562
332 | 3.4072 | 0 | 0 | 97.1574 | 91.455 | 101493.7272 | 20 | 22.1951 | 26.1199 | 27.2814 | 90.1636 | 79.433 | 4.2 | 40 | 0.25253 | 93.2963 | 6519.901
334 | 3.3406 | 0 | 0 | 93.1154 | 92.4036 | 101504.5233 | 20 | 22.2252 | 26.1631 | 27.2924 | 90.2088 | 79.398 | 4.2 | 40 | 0.24759 | 91.7756 | 6420.9296
336 | 3.3268 | 0 | 0 | 93.8288 | 90.1398 | 101498.9986 | 20 | 22.1921 | 26.1611 | 27.2764 | 90.3031 | 79.401 | 4.2 | 40 | 0.24657 | 92.1186 | 6440.8585
338 | 3.3668 | 0 | 0 | 101.0028 | 95.5409 | 101495.7368 | 20 | 22.179 | 26.1159 | 27.2914 | 90.1837 | 79.407 | 4.2 | 40 | 0.24953 | 92.4711 | 6463.348
340 | 3.3421 | 0 | 0 | 94.6257 | 87.8737 | 101497.995 | 20 | 22.166 | 26.1098 | 27.2663 | 90.0812 | 79.43 | 4.2 | 40 | 0.2477 | 91.957 | 6423.3687
342 | 3.3672 | 0 | 0 | 94.8321 | 88.6667 | 101500.5064 | 20 | 22.2222 | 26.152 | 27.2944 | 90.1445 | 79.446 | 4.2 | 40 | 0.24957 | 92.3192 | 6453.2064
344 | 3.3416 | 0 | 0 | 99.1867 | 94.6416 | 101496.2386 | 20 | 22.2132 | 26.1239 | 27.2924 | 90.2037 | 79.399 | 4.2 | 40 | 0.24766 | 91.1705 | 6377.1434
346 | 3.3569 | 0 | 0 | 93.8455 | 87.1269 | 101495.7368 | 20 | 22.2001 | 26.145 | 27.3115 | 90.023 | 79.38 | 4.2 | 40 | 0.2488 | 92.3879 | 6462.9649
348 | 3.3529 | 0 | 0 | 94.2872 | 88.7054 | 101499.5027 | 20 | 22.174 | 26.138 | 27.2924 | 89.9879 | 79.268 | 4.2 | 40 | 0.24851 | 92.7258 | 6496.3612
350 | 3.3524 | 0 | 0 | 95.7367 | 93.6968 | 101504.5233 | 20 | 22.2041 | 26.1359 | 27.2794 | 89.9136 | 79.263 | 4.2 | 40 | 0.24847 | 91.9602 | 6446.6912
352 | 3.3436 | 0 | 0 | 93.0783 | 89.5812 | 101495.2327 | 20 | 22.1991 | 26.149 | 27.3256 | 89.7911 | 79.204 | 4.2 | 40 | 0.24781 | 92.1382 | 6465.2884
354 | 3.3668 | 0 | 0 | 99.7771 | 94.6629 | 101493.4763 | 20 | 22.2041 | 26.1359 | 27.2683 | 89.8584 | 79.146 | 4.2 | 40 | 0.24953 | 92.353 | 6487.5297
356 | 3.3396 | 0 | 0 | 94.5513 | 88.2175 | 101501.0082 | 20 | 22.171 | 26.1038 | 27.2743 | 89.9618 | 79.114 | 4.2 | 40 | 0.24752 | 91.6317 | 6436.7288
358 | 3.3668 | 0 | 0 | 95.8452 | 88.3905 | 101500.7573 | 20 | 22.2072 | 26.1249 | 27.2583 | 89.9397 | 79.09 | 4.2 | 40 | 0.24953 | 92.0227 | 6471.0333
360 | 3.3653 | 0 | 0 | 99.2011 | 95.695 | 101495.9877 | 20 | 22.2102 | 26.1279 | 27.2844 | 90.1656 | 79.069 | 4.2 | 40 | 0.24942 | 91.9821 | 6470.9122
362 | 3.3134 | 0 | 0 | 94.3342 | 86.8848 | 101494.4799 | 20 | 22.1891 | 26.1068 | 27.2794 | 90.1736 | 79.057 | 4.2 | 40 | 0.24558 | 90.5653 | 6370.2234
364 | 3.3796 | 0 | 0 | 97.2644 | 88.5628 | 101494.4799 | 20 | 22.1981 | 26.1229 | 27.2884 | 90.0652 | 79.09 | 4.2 | 40 | 0.25048 | 92.5393 | 6506.3296
366 | 3.3401 | 0 | 0 | 94.9611 | 94.3881 | 101501.2591 | 20 | 22.173 | 26.0968 | 27.2502 | 90.1867 | 78.949 | 4.2 | 40 | 0.24755 | 91.4346 | 6441.7804
368 | 3.3139 | 0 | 0 | 94.3563 | 89.5486 | 101500.5064 | 20 | 22.2303 | 26.156 | 27.2944 | 90.3192 | 78.886 | 4.2 | 40 | 0.24561 | 90.7645 | 6408.1414
370 | 3.4221 | 0 | 0 | 98.6987 | 91.3912 | 101491.9708 | 20 | 22.2303 | 26.1279 | 27.2834 | 90.4969 | 78.915 | 4.2 | 40 | 0.25363 | 93.0543 | 6566.4442
372 | 3.4334 | 0 | 0 | 93.4858 | 89.1312 | 101493.2254 | 20 | 22.1861 | 26.1169 | 27.2894 | 90.2901 | 78.873 | 4.2 | 40 | 0.25447 | 94.1572 | 6644.0176
374 | 3.3396 | 0 | 0 | 94.1817 | 89.8377 | 101497.995 | 20 | 22.2162 | 26.1189 | 27.2884 | 90.4487 | 78.845 | 4.2 | 40 | 0.24752 | 90.9294 | 6422.8385
376 | 3.3944 | 0 | 0 | 99.2277 | 96.7218 | 101496.4895 | 20 | 22.1901 | 26.1048 | 27.2884 | 90.3483 | 79.007 | 4.2 | 40 | 0.25158 | 92.7071 | 6526.7222
378 | 3.3811 | 0 | 0 | 93.01 | 89.78 | 101496.2386 | 20 | 22.2323 | 26.1179 | 27.2603 | 90.3322 | 79.092 | 4.2 | 40 | 0.25059 | 91.6557 | 6447.8451
380 | 3.3663 | 0 | 0 | 95.0772 | 92.2738 | 101495.7368 | 20 | 22.2433 | 26.1359 | 27.3205 | 90.3945 | 79.051 | 4.2 | 40 | 0.24949 | 91.4192 | 6437.1052
382 | 3.4216 | 0 | 0 | 97.8571 | 92.8916 | 101498.4968 | 20 | 22.2242 | 26.152 | 27.2934 | 90.1616 | 78.915 | 4.2 | 40 | 0.25359 | 93.7601 | 6615.5475
384 | 3.4072 | 0 | 0 | 94.5513 | 89.1501 | 101498.2459 | 20 | 22.1991 | 26.1068 | 27.2583 | 89.8543 | 78.971 | 4.2 | 40 | 0.25253 | 92.8904 | 6544.8212
386 | 3.3263 | 0 | 0 | 100.174 | 92.7588 | 101497.2422 | 20 | 22.2403 | 26.1329 | 27.2743 | 89.8594 | 78.922 | 4.2 | 40 | 0.24653 | 90.3332 | 6374.7731
388 | 3.3534 | 0 | 0 | 94.1658 | 87.0161 | 101499.5027 | 20 | 22.2353 | 26.139 | 27.2904 | 89.9598 | 78.927 | 4.2 | 40 | 0.24854 | 91.3292 | 6443.9182
390 | 3.3411 | 0 | 0 | 93.3082 | 88.7548 | 101501.0082 | 20 | 22.2102 | 26.152 | 27.2904 | 89.7218 | 78.812 | 4.2 | 40 | 0.24763 | 91.8828 | 6493.2737
392 | 3.3707 | 0 | 0 | 99.7733 | 97.3357 | 101496.2386 | 20 | 22.2052 | 26.1279 | 27.2553 | 89.6525 | 78.79 | 4.2 | 40 | 0.24982 | 92.2487 | 6521.0854
394 | 3.3401 | 0 | 0 | 94.6682 | 87.6665 | 101492.9745 | 20 | 22.1941 | 26.0847 | 27.2502 | 89.7891 | 78.727 | 4.2 | 40 | 0.24755 | 90.6621 | 6414.8242
396 | 3.3934 | 0 | 0 | 94.7577 | 88.2842 | 101498.4968 | 20 | 22.2273 | 26.141 | 27.2884 | 89.9979 | 78.681 | 4.2 | 40 | 0.2515 | 92.6561 | 6565.1004
398 | 3.3702 | 0 | 0 | 97.9596 | 94.0823 | 101498.7477 | 20 | 22.1961 | 26.1008 | 27.2693 | 90.029 | 78.681 | 4.2 | 40 | 0.24979 | 91.8101 | 6501.5725
400 | 3.3924 | 0 | 0 | 94.461 | 87.6005 | 101496.2386 | 20 | 22.1991 | 26.0666 | 27.2452 | 89.8051 | 78.621 | 4.2 | 40 | 0.25143 | 91.5358 | 6489.3824
402 | 3.3406 | 0 | 0 | 95.4195 | 89.0196 | 101498.7477 | 20 | 22.2031 | 26.0757 | 27.2432 | 89.3965 | 78.436 | 4.2 | 40 | 0.24759 | 90.2541 | 6420.0256
404 | 3.3144 | 0 | 0 | 93.4797 | 92.2533 | 101500.5064 | 20 | 22.2112 | 26.1048 | 27.2382 | 88.9066 | 78.367 | 4.2 | 40 | 0.24565 | 90.0348 | 6413.2142
406 | 3.3421 | 0 | 0 | 93.6391 | 89.1426 | 101502.2628 | 20 | 22.2031 | 26.1128 | 27.2673 | 88.8011 | 78.392 | 4.2 | 40 | 0.2477 | 91.1606 | 6489.5834
408 | 3.3282 | 0 | 0 | 100.0177 | 94.6097 | 101492.9745 | 20 | 22.2052 | 26.1199 | 27.2643 | 88.8865 | 78.379 | 4.2 | 40 | 0.24668 | 90.9001 | 6472.7715
410 | 3.345 | 0 | 0 | 93.7393 | 88.5779 | 101500.0046 | 20 | 22.2052 | 26.0767 | 27.2613 | 88.6325 | 78.259 | 4.2 | 40 | 0.24792 | 90.3507 | 6447.4195
412 | 3.3544 | 0 | 0 | 93.394 | 87.5952 | 101505.276 | 20 | 22.2484 | 26.139 | 27.3004 | 88.6224 | 78.519 | 4.2 | 40 | 0.24861 | 91.0504 | 6472.3227
414 | 3.3134 | 0 | 0 | 98.0939 | 96.7552 | 101502.7669 | 20 | 22.2564 | 26.157 | 27.2814 | 88.5411 | 78.489 | 4.2 | 40 | 0.24558 | 90.1703 | 6414.094
416 | 3.3263 | 0 | 0 | 93.7415 | 88.8193 | 101495.7368 | 20 | 22.2132 | 26.1068 | 27.2834 | 88.515 | 78.508 | 4.2 | 40 | 0.24653 | 90.3567 | 6420.2476
418 | 3.3426 | 0 | 0 | 97.2386 | 88.5666 | 101501.7609 | 20 | 22.2082 | 26.1339 | 27.2693 | 88.7379 | 78.73 | 4.2 | 40 | 0.24774 | 91.5488 | 6478.83
420 | 3.3534 | 0 | 0 | 96.5738 | 92.8293 | 101507.5365 | 20 | 22.2192 | 26.142 | 27.2673 | 88.6827 | 78.84 | 4.2 | 40 | 0.24854 | 91.7757 | 6483.537
422 | 3.3668 | 0 | 0 | 95.2533 | 88.4148 | 101498.7477 | 20 | 22.2463 | 26.15 | 27.2914 | 88.8252 | 79.093 | 4.2 | 40 | 0.24953 | 91.6922 | 6451.8981
424 | 3.3539 | 0 | 0 | 96.8455 | 90.7014 | 101492.9745 | 20 | 22.2413 | 26.1691 | 27.3045 | 88.8754 | 79.227 | 4.2 | 40 | 0.24858 | 91.9067 | 6451.2149
426 | 3.3579 | 0 | 0 | 93.1397 | 91.3161 | 101506.0287 | 20 | 22.2102 | 26.139 | 27.2914 | 89.0019 | 79.256 | 4.2 | 40 | 0.24887 | 92.0385 | 6453.6561
428 | 3.3529 | 0 | 0 | 93.6619 | 90.3659 | 101503.7705 | 20 | 22.2323 | 26.147 | 27.2934 | 89.0602 | 79.227 | 4.2 | 40 | 0.24851 | 91.5743 | 6426.8587
430 | 3.3475 | 0 | 0 | 99.0471 | 96.0403 | 101501.7609 | 20 | 22.2433 | 26.1982 | 27.3316 | 89.0793 | 79.198 | 4.2 | 40 | 0.2481 | 92.3642 | 6486.8561
432 | 3.3282 | 0 | 0 | 95.0271 | 89.645 | 101495.4836 | 20 | 22.2052 | 26.1661 | 27.3336 | 88.8945 | 79.135 | 4.2 | 40 | 0.24668 | 91.9729 | 6462.1949
434 | 3.3406 | 0 | 0 | 95.3755 | 89.7125 | 101501.51 | 20 | 22.2021 | 26.145 | 27.3095 | 88.7118 | 78.901 | 4.2 | 40 | 0.24759 | 91.8927 | 6482.8611
436 | 3.3672 | 0 | 0 | 96.274 | 93.0085 | 101502.7669 | 20 | 22.1891 | 26.147 | 27.3175 | 88.5511 | 78.754 | 4.2 | 40 | 0.24957 | 92.98 | 6575.1018
438 | 3.3801 | 0 | 0 | 93.2642 | 89.8741 | 101496.7404 | 20 | 22.18 | 26.1179 | 27.3065 | 88.3915 | 78.733 | 4.2 | 40 | 0.25052 | 92.8608 | 6568.0582
440 | 3.3954 | 0 | 0 | 101.6251 | 95.6821 | 101492.4726 | 20 | 22.2463 | 26.1681 | 27.3205 | 88.2158 | 79.095 | 4.2 | 40 | 0.25165 | 92.9003 | 6536.6761
442 | 3.4211 | 0 | 0 | 95.3611 | 88.0649 | 101502.0119 | 20 | 22.2202 | 26.1862 | 27.3125 | 88.274 | 79.408 | 4.2 | 40 | 0.25355 | 94.6576 | 6620.828
444 | 3.3796 | 0 | 0 | 94.6295 | 89.3353 | 101505.276 | 20 | 22.2222 | 26.1962 | 27.3517 | 88.2499 | 79.531 | 4.2 | 40 | 0.25048 | 93.6996 | 6539.986
446 | 3.3386 | 0 | 0 | 99.9562 | 97.1399 | 101499.7536 | 20 | 22.2082 | 26.2083 | 27.3577 | 88.5672 | 79.543 | 4.2 | 40 | 0.24744 | 93.1719 | 6500.1918
448 | 3.3401 | 0 | 0 | 95.0803 | 88.5134 | 101498.2459 | 20 | 22.2273 | 26.2334 | 27.3517 | 88.9678 | 79.412 | 4.2 | 40 | 0.24755 | 93.3536 | 6529.9655
450 | 3.3529 | 0 | 0 | 95.9181 | 88.2736 | 101499.2518 | 20 | 22.2443 | 26.2464 | 27.4079 | 89.1797 | 79.372 | 4.2 | 40 | 0.24851 | 93.6183 | 6555.0225
452 | 3.3761 | 0 | 0 | 96.8978 | 95.7079 | 101506.5328 | 20 | 22.2242 | 26.2093 | 27.3818 | 89.1044 | 79.267 | 4.2 | 40 | 0.25022 | 93.8641 | 6582.0155
454 | 3.3668 | 0 | 0 | 94.5809 | 90.7082 | 101497.4932 | 20 | 22.2052 | 26.2193 | 27.3768 | 89.3574 | 79.329 | 4.2 | 40 | 0.24953 | 94.2875 | 6602.3239
456 | 3.4058 | 0 | 0 | 99.1905 | 93.2293 | 101493.7272 | 20 | 22.2624 | 26.2725 | 27.3978 | 89.6806 | 79.298 | 4.2 | 40 | 0.25242 | 95.2841 | 6682.4306
458 | 3.3811 | 0 | 0 | 96.0995 | 89.7019 | 101504.7742 | 20 | 22.2604 | 26.2575 | 27.3798 | 90.0009 | 79.327 | 4.2 | 40 | 0.25059 | 94.2854 | 6608.7978
460 | 3.349 | 0 | 0 | 94.8131 | 88.5544 | 101504.2724 | 20 | 22.2473 | 26.2394 | 27.4149 | 90.1234 | 79.393 | 4.2 | 40 | 0.24821 | 93.2733 | 6528.8105
462 | 3.3786 | 0 | 0 | 100.1247 | 96.6853 | 101496.7404 | 20 | 22.2252 | 26.2203 | 27.3717 | 89.9367 | 79.371 | 4.2 | 40 | 0.25041 | 94.1694 | 6591.5248
464 | 3.3524 | 0 | 0 | 94.8116 | 88.0733 | 101498.2459 | 20 | 22.2273 | 26.2314 | 27.3667 | 90.1646 | 79.435 | 4.2 | 40 | 0.24847 | 93.6515 | 6548.1691
466 | 3.3663 | 0 | 0 | 94.3608 | 89.7709 | 101504.5233 | 20 | 22.2604 | 26.2575 | 27.3988 | 90.1957 | 79.464 | 4.2 | 40 | 0.24949 | 93.8724 | 6564.0895
468 | 3.3934 | 0 | 0 | 98.3102 | 95.846 | 101501.51 | 20 | 22.2252 | 26.2525 | 27.3778 | 90.2248 | 79.566 | 4.2 | 40 | 0.2515 | 95.3432 | 6650.9869
470 | 3.4082 | 0 | 0 | 95.9477 | 90.0191 | 101502.5137 | 20 | 22.2062 | 26.2012 | 27.3667 | 90.3081 | 79.618 | 4.2 | 40 | 0.2526 | 94.9951 | 6618.5042
472 | 3.4354 | 0 | 0 | 99.4774 | 91.6811 | 101500.2555 | 20 | 22.2112 | 26.2223 | 27.3717 | 90.4557 | 79.701 | 4.2 | 40 | 0.25461 | 96.1371 | 6688.9852
474 | 3.3554 | 0 | 0 | 96.8675 | 93.5617 | 101508.2892 | 20 | 22.2443 | 26.2404 | 27.3768 | 90.4969 | 79.687 | 4.2 | 40 | 0.24869 | 93.5461 | 6514.0493
476 | 3.3806 | 0 | 0 | 93.7787 | 89.6776 | 101505.0251 | 20 | 22.2393 | 26.2665 | 27.425 | 90.4537 | 79.591 | 4.2 | 40 | 0.25055 | 94.9825 | 6624.5618
478 | 3.3658 | 0 | 0 | 99.8819 | 95.7534 | 101495.2327 | 20 | 22.2232 | 26.2374 | 27.3928 | 90.516 | 79.531 | 4.2 | 40 | 0.24946 | 94.2598 | 6579.1986
480 | 3.3663 | 0 | 0 | 93.7757 | 90.7279 | 101505.5269 | 20 | 22.1981 | 26.2324 | 27.3527 | 90.2238 | 79.589 | 4.2 | 40 | 0.24949 | 94.7454 | 6603.5195
482 | 3.3514 | 0 | 0 | 94.395 | 90.6278 | 101501.51 | 20 | 22.2293 | 26.2525 | 27.4129 | 90.0521 | 79.519 | 4.2 | 40 | 0.2484 | 94.0701 | 6568.0252
484 | 3.3806 | 0 | 0 | 98.8839 | 95.4597 | 101505.7778 | 20 | 22.2403 | 26.2665 | 27.4019 | 89.8814 | 79.677 | 4.2 | 40 | 0.25055 | 94.9588 | 6613.1086
486 | 3.3687 | 0 | 0 | 95.5273 | 89.3391 | 101497.4932 | 20 | 22.2463 | 26.2504 | 27.4179 | 89.9608 | 79.721 | 4.2 | 40 | 0.24968 | 94.1066 | 6549.4329
488 | 3.3672 | 0 | 0 | 96.0934 | 90.7606 | 101501.2591 | 20 | 22.1941 | 26.2213 | 27.4089 | 89.7891 | 79.784 | 4.2 | 40 | 0.24957 | 94.6081 | 6571.1592
490 | 3.3811 | 0 | 0 | 95.8164 | 94.0937 | 101504.2724 | 20 | 22.2202 | 26.2133 | 27.3737 | 89.7098 | 79.857 | 4.2 | 40 | 0.25059 | 94.1908 | 6536.855
492 | 3.3786 | 0 | 0 | 94.2621 | 91.0361 | 101506.2797 | 20 | 22.2584 | 26.2625 | 27.43 | 89.7027 | 79.988 | 4.2 | 40 | 0.25041 | 94.3823 | 6539.6144
494 | 3.3539 | 0 | 0 | 100.0063 | 94.3563 | 101494.7308 | 20 | 22.2283 | 26.2956 | 27.3999 | 89.9276 | 79.967 | 4.2 | 40 | 0.24858 | 95.1736 | 6593.3948
496 | 3.3278 | 0 | 0 | 96.183 | 90.7302 | 101511.5534 | 20 | 22.2443 | 26.2846 | 27.4209 | 90.0561 | 79.967 | 4.2 | 40 | 0.24664 | 93.8014 | 6500.1404
498 | 3.3534 | 0 | 0 | 96.0198 | 88.6174 | 101502.7669 | 20 | 22.2102 | 26.2464 | 27.4009 | 90.1485 | 79.947 | 4.2 | 40 | 0.24854 | 94.4311 | 6542.1767
500 | 3.3519 | 0 | 0 | 99.9707 | 97.3274 | 101505.5269 | 20 | 22.2353 | 26.2756 | 27.441 | 90.2288 | 79.909 | 4.2 | 40 | 0.24843 | 94.4833 | 6552.9551
502 | 3.3391 | 0 | 0 | 93.2149 | 91.2281 | 101504.7742 | 20 | 22.2684 | 26.2645 | 27.425 | 90.4156 | 79.897 | 4.2 | 40 | 0.24748 | 93.0918 | 6461.5065
504 | 3.3505 | 0 | 0 | 95.4127 | 89.1843 | 101510.8006 | 20 | 22.2574 | 26.2836 | 27.446 | 90.4939 | 79.825 | 4.2 | 40 | 0.24832 | 94.1127 | 6539.2809
506 | 3.4102 | 0 | 0 | 98.9955 | 96.3666 | 101510.2988 | 20 | 22.2343 | 26.2675 | 27.443 | 90.5712 | 79.796 | 4.2 | 40 | 0.25275 | 95.9581 | 6668.1909
508 | 3.3801 | 0 | 0 | 95.6024 | 88.1029 | 101507.2856 | 20 | 22.2554 | 26.2223 | 27.4029 | 90.6786 | 79.74 | 4.2 | 40 | 0.25052 | 93.5473 | 6509.3805
510 | 3.3924 | 0 | 0 | 96.1541 | 89.6488 | 101505.5269 | 20 | 22.2865 | 26.2585 | 27.4069 | 90.5672 | 79.689 | 4.2 | 40 | 0.25143 | 94.0077 | 6550.7737
512 | 3.3273 | 0 | 0 | 97.4238 | 94.911 | 101508.2892 | 20 | 22.3046 | 26.2725 | 27.4129 | 90.4768 | 79.565 | 4.2 | 40 | 0.2466 | 92.1084 | 6434.3532
514 | 3.2996 | 0 | 0 | 93.6315 | 89.9667 | 101505.0251 | 20 | 22.2443 | 26.2454 | 27.3838 | 90.2369 | 79.295 | 4.2 | 40 | 0.24455 | 92.1064 | 6457.8633
516 | 3.3179 | 0 | 0 | 100.3015 | 94.7008 | 101501.0082 | 20 | 22.2494 | 26.2233 | 27.3788 | 89.766 | 79.08 | 4.2 | 40 | 0.24591 | 91.9886 | 6474.5762
518 | 3.3924 | 0 | 0 | 94.0405 | 89.5713 | 101503.7705 | 20 | 22.2383 | 26.2022 | 27.3567 | 89.4668 | 78.956 | 4.2 | 40 | 0.25143 | 93.8177 | 6616.4681
520 | 3.3376 | 0 | 0 | 94.0739 | 89.4051 | 101508.2892 | 20 | 22.2715 | 26.2474 | 27.3999 | 89.1756 | 78.927 | 4.2 | 40 | 0.24737 | 92.5827 | 6536.5314
522 | 3.3406 | 0 | 0 | 98.682 | 98.0833 | 101502.7669 | 20 | 22.2524 | 26.2133 | 27.3948 | 88.9718 | 78.917 | 4.2 | 40 | 0.24759 | 92.3138 | 6516.5048
524 | 3.3411 | 0 | 0 | 95.6806 | 90.2915 | 101501.7609 | 20 | 22.2132 | 26.2183 | 27.3617 | 89.0632 | 78.912 | 4.2 | 40 | 0.24763 | 93.3577 | 6586.2219
526 | 3.3366 | 0 | 0 | 96.2133 | 88.1051 | 101512.3061 | 20 | 22.2413 | 26.2153 | 27.3436 | 89.0893 | 78.898 | 4.2 | 40 | 0.2473 | 92.5087 | 6531.1742
528 | 3.3786 | 0 | 0 | 97.9262 | 95.2996 | 101505.7778 | 20 | 22.2634 | 26.2344 | 27.3808 | 88.9337 | 78.89 | 4.2 | 40 | 0.25041 | 93.601 | 6611.8091
530 | 3.3677 | 0 | 0 | 95.6904 | 89.5956 | 101500.5064 | 20 | 22.2353 | 26.2022 | 27.3808 | 88.8132 | 78.898 | 4.2 | 40 | 0.2496 | 93.2059 | 6579.6996
532 | 3.3129 | 0 | 0 | 97.4685 | 90.4775 | 101501.51 | 20 | 22.2192 | 26.1992 | 27.3597 | 88.7299 | 78.866 | 4.2 | 40 | 0.24554 | 91.9911 | 6495.7684
534 | 3.3307 | 0 | 0 | 94.0163 | 93.7696 | 101500.2555 | 20 | 22.2694 | 26.2354 | 27.3527 | 88.7138 | 78.854 | 4.2 | 40 | 0.24686 | 92.1576 | 6514.6854
536 | 3.3406 | 0 | 0 | 94.5695 | 90.057 | 101504.2724 | 20 | 22.2684 | 26.2565 | 27.3968 | 88.7941 | 78.855 | 4.2 | 40 | 0.24759 | 92.9458 | 6570.1679
538 | 3.3569 | 0 | 0 | 101.7715 | 95.3778 | 101497.7441 | 20 | 22.2383 | 26.2474 | 27.3918 | 88.6325 | 79.014 | 4.2 | 40 | 0.2488 | 93.8932 | 6615.0249
540 | 3.344 | 0 | 0 | 93.4273 | 88.8861 | 101504.7742 | 20 | 22.2303 | 26.2042 | 27.3878 | 88.6897 | 79.144 | 4.2 | 40 | 0.24785 | 92.714 | 6516.1098
542 | 3.3529 | 0 | 0 | 93.5556 | 88.9574 | 101505.276 | 20 | 22.2283 | 26.2324 | 27.3898 | 89.1505 | 79.256 | 4.2 | 40 | 0.24851 | 93.6654 | 6569.8097
544 | 3.3406 | 0 | 0 | 97.3911 | 96.6193 | 101502.5137 | 20 | 22.2865 | 26.2796 | 27.4009 | 89.1937 | 79.421 | 4.2 | 40 | 0.24759 | 93.0628 | 6515.3487
546 | 3.3663 | 0 | 0 | 95.4468 | 90.2953 | 101504.7742 | 20 | 22.3036 | 26.2866 | 27.445 | 89.4417 | 79.506 | 4.2 | 40 | 0.24949 | 93.5419 | 6541.12
548 | 3.3672 | 0 | 0 | 98.7739 | 89.6753 | 101495.9877 | 20 | 22.2664 | 26.2856 | 27.432 | 89.7017 | 79.714 | 4.2 | 40 | 0.24957 | 94.419 | 6574.2728
550 | 3.3672 | 0 | 0 | 96.7043 | 93.6672 | 101505.7778 | 20 | 22.2443 | 26.2886 | 27.438 | 90.1535 | 79.868 | 4.2 | 40 | 0.24957 | 95.009 | 6595.1363
552 | 3.3924 | 0 | 0 | 94.1847 | 89.5243 | 101501.2591 | 20 | 22.2996 | 26.3177 | 27.443 | 90.4146 | 79.978 | 4.2 | 40 | 0.25143 | 95.1011 | 6595.2648
554 | 3.3273 | 0 | 0 | 100.3327 | 96.5161 | 101501.0082 | 20 | 22.3046 | 26.3017 | 27.435 | 90.7057 | 80.07 | 4.2 | 40 | 0.2466 | 92.7845 | 6424.9224
556 | 3.3658 | 0 | 0 | 91.7957 | 89.0978 | 101501.7609 | 20 | 22.3157 | 26.3208 | 27.4591 | 91.025 | 80.063 | 4.2 | 40 | 0.24946 | 94.0471 | 6514.3842
558 | 3.3993 | 0 | 0 | 95.402 | 88.2751 | 101507.0347 | 20 | 22.2614 | 26.3077 | 27.4591 | 91.0371 | 80.178 | 4.2 | 40 | 0.25194 | 95.9619 | 6627.5965
560 | 3.3144 | 0 | 0 | 99.7346 | 95.6897 | 101499.5027 | 20 | 22.2614 | 26.2756 | 27.438 | 90.8634 | 80.034 | 4.2 | 40 | 0.24565 | 92.8216 | 6426.6905
562 | 3.3534 | 0 | 0 | 94.1035 | 89.5698 | 101503.0178 | 20 | 22.2554 | 26.2836 | 27.438 | 90.5421 | 79.953 | 4.2 | 40 | 0.24854 | 94.2429 | 6533.575
564 | 3.3539 | 0 | 0 | 94.4511 | 91.5248 | 101499.7536 | 20 | 22.2996 | 26.3318 | 27.4641 | 90.3332 | 79.802 | 4.2 | 40 | 0.24858 | 94.3507 | 6563.2494
566 | 3.3816 | 0 | 0 | 97.6332 | 93.7082 | 101504.7742 | 20 | 22.2664 | 26.2997 | 27.4621 | 90.0361 | 79.656 | 4.2 | 40 | 0.25063 | 95.1523 | 6632.0246
568 | 3.3539 | 0 | 0 | 94.3722 | 90.1026 | 101504.7742 | 20 | 22.2283 | 26.2675 | 27.439 | 90.0943 | 79.577 | 4.2 | 40 | 0.24858 | 94.5155 | 6592.3343
570 | 3.3006 | 0 | 0 | 100.5156 | 93.4251 | 101496.2386 | 20 | 22.2343 | 26.2725 | 27.444 | 90.0792 | 79.679 | 4.2 | 40 | 0.24463 | 92.9897 | 6475.0762
572 | 3.3603 | 0 | 0 | 92.2655 | 90.7355 | 101498.4968 | 20 | 22.2755 | 26.2896 | 27.424 | 90.0792 | 79.65 | 4.2 | 40 | 0.24905 | 94.1075 | 6560.9241
574 | 3.3939 | 0 | 0 | 94.2523 | 90.1208 | 101504.0214 | 20 | 22.2504 | 26.3167 | 27.4531 | 90.1284 | 79.646 | 4.2 | 40 | 0.25154 | 96.2844 | 6710.221
576 | 3.3806 | 0 | 0 | 100.3547 | 96.4334 | 101500.2555 | 20 | 22.2755 | 26.3057 | 27.4621 | 90.2148 | 79.687 | 4.2 | 40 | 0.25055 | 95.0534 | 6622.5973
578 | 3.3707 | 0 | 0 | 95.125 | 87.2658 | 101494.7308 | 20 | 22.2534 | 26.2685 | 27.435 | 90.1314 | 79.722 | 4.2 | 40 | 0.24982 | 94.4214 | 6572.0343
580 | 3.3401 | 0 | 0 | 94.4185 | 89.629 | 101507.5365 | 20 | 22.2865 | 26.3248 | 27.4631 | 89.9096 | 79.687 | 4.2 | 40 | 0.24755 | 94.1023 | 6557.5973
582 | 3.3534 | 0 | 0 | 98.0559 | 96.3408 | 101505.0251 | 20 | 22.2986 | 26.3198 | 27.4842 | 89.9216 | 79.669 | 4.2 | 40 | 0.24854 | 94.0782 | 6559.3549
584 | 3.3406 | 0 | 0 | 95.6426 | 90.5405 | 101501.51 | 20 | 22.2775 | 26.3157 | 27.4762 | 89.8935 | 79.714 | 4.2 | 40 | 0.24759 | 94.1162 | 6554.4498
586 | 3.3534 | 0 | 0 | 98.9583 | 91.5005 | 101501.51 | 20 | 22.2745 | 26.3017 | 27.4521 | 89.7278 | 79.697 | 4.2 | 40 | 0.24854 | 94.2193 | 6563.2315
588 | 3.3643 | 0 | 0 | 94.6021 | 89.9318 | 101500.2555 | 20 | 22.3237 | 26.3378 | 27.4661 | 89.529 | 79.658 | 4.2 | 40 | 0.24935 | 94.2178 | 6573.2212
590 | 3.3406 | 0 | 0 | 93.9191 | 89.9903 | 101500.0046 | 20 | 22.3498 | 26.3509 | 27.4842 | 89.6405 | 79.735 | 4.2 | 40 | 0.24759 | 93.2497 | 6499.9168
592 | 3.3534 | 0 | 0 | 102.0326 | 96.3416 | 101497.995 | 20 | 22.2946 | 26.3398 | 27.4812 | 89.777 | 79.844 | 4.2 | 40 | 0.24854 | 94.6422 | 6578.1509
594 | 3.3979 | 0 | 0 | 95.1311 | 89.5304 | 101502.7669 | 20 | 22.2725 | 26.2966 | 27.444 | 89.775 | 79.737 | 4.2 | 40 | 0.25183 | 95.3963 | 6640.3606
596 | 3.3273 | 0 | 0 | 93.9616 | 89.0462 | 101505.276 | 20 | 22.2805 | 26.3077 | 27.4621 | 89.8413 | 79.803 | 4.2 | 40 | 0.2466 | 93.4841 | 6500.6985
598 | 3.3544 | 0 | 0 | 98.5553 | 96.5336 | 101498.7477 | 20 | 22.3167 | 26.3459 | 27.4681 | 90.022 | 79.893 | 4.2 | 40 | 0.24861 | 94.2939 | 6550.8791
600 | 3.3396 | 0 | 0 | 94.5733 | 89.9804 | 101493.7272 | 20 | 22.2835 | 26.3157 | 27.4541 | 90.2088 | 79.927 | 4.2 | 40 | 0.24752 | 93.9479 | 6519.2394
602 | 3.3663 | 0 | 0 | 97.7516 | 89.311 | 101504.0214 | 20 | 22.2775 | 26.3057 | 27.4681 | 90.271 | 79.956 | 4.2 | 40 | 0.24949 | 94.6035 | 6560.7475
604 | 3.3539 | 0 | 0 | 97.2538 | 94.2963 | 101499.7536 | 20 | 22.2765 | 26.2966 | 27.4611 | 90.3945 | 80.001 | 4.2 | 40 | 0.24858 | 94.0688 | 6518.4606
606 | 3.3544 | 0 | 0 | 94.4557 | 89.8719 | 101496.2386 | 20 | 22.2514 | 26.2997 | 27.4581 | 90.4417 | 80.08 | 4.2 | 40 | 0.24861 | 94.7408 | 6553.2112
608 | 3.3426 | 0 | 0 | 99.2368 | 94.5369 | 101496.4895 | 20 | 22.3217 | 26.3479 | 27.4701 | 90.6184 | 80.221 | 4.2 | 40 | 0.24774 | 93.8906 | 6486.4719
610 | 3.3401 | 0 | 0 | 96.1458 | 90.3249 | 101501.0082 | 20 | 22.2875 | 26.3569 | 27.4882 | 90.4216 | 80.249 | 4.2 | 40 | 0.24755 | 94.8279 | 6544.1997
612 | 3.3944 | 0 | 0 | 95.0605 | 88.4702 | 101504.5233 | 20 | 22.2966 | 26.3208 | 27.4561 | 90.3423 | 80.279 | 4.2 | 40 | 0.25158 | 95.2992 | 6574.351
614 | 3.3282 | 0 | 0 | 99.4045 | 97.3691 | 101495.9877 | 20 | 22.3267 | 26.3368 | 27.4661 | 90.3172 | 80.143 | 4.2 | 40 | 0.24668 | 93.1152 | 6442.1407
616 | 3.3934 | 0 | 0 | 93.4782 | 89.0022 | 101493.4763 | 20 | 22.3157 | 26.3469 | 27.5043 | 90.026 | 80.047 | 4.2 | 40 | 0.2515 | 95.4378 | 6612.5498
618 | 3.3332 | 0 | 0 | 94.3919 | 90.7188 | 101498.7477 | 20 | 22.3046 | 26.3499 | 27.4852 | 89.9517 | 80.001 | 4.2 | 40 | 0.24704 | 94.0709 | 6521.7892
620 | 3.3949 | 0 | 0 | 98.4392 | 95.2116 | 101501.7609 | 20 | 22.2855 | 26.3228 | 27.4772 | 89.9708 | 79.962 | 4.2 | 40 | 0.25161 | 95.6223 | 6631.6339
622 | 3.3278 | 0 | 0 | 94.9125 | 89.7451 | 101496.2386 | 20 | 22.2634 | 26.2966 | 27.4641 | 90.2037 | 79.931 | 4.2 | 40 | 0.24664 | 93.638 | 6495.0214
624 | 3.3006 | 0 | 0 | 98.871 | 90.2407 | 101491.9708 | 20 | 22.3126 | 26.3368 | 27.4802 | 90.1756 | 79.938 | 4.2 | 40 | 0.24463 | 92.6656 | 6432.2774
626 | 3.312 | 0 | 0 | 94.8754 | 93.0578 | 101503.0178 | 20 | 22.3167 | 26.3429 | 27.4812 | 89.9437 | 79.906 | 4.2 | 40 | 0.24547 | 93.0308 | 6461.668
628 | 3.3801 | 0 | 0 | 93.3446 | 89.1335 | 101497.995 | 20 | 22.2865 | 26.3348 | 27.4772 | 89.8975 | 79.816 | 4.2 | 40 | 0.25052 | 95.4657 | 6637.689
630 | 3.3648 | 0 | 0 | 99.5077 | 97.9315 | 101495.9877 | 20 | 22.2725 | 26.3258 | 27.4631 | 89.7359 | 79.766 | 4.2 | 40 | 0.24938 | 95.1515 | 6619.9753
632 | 3.388 | 0 | 0 | 94.5096 | 89.5175 | 101496.7404 | 20 | 22.3026 | 26.3047 | 27.4711 | 89.5541 | 79.664 | 4.2 | 40 | 0.2511 | 94.5967 | 6596.5406
634 | 3.3549 | 0 | 0 | 94.4048 | 89.1509 | 101501.0082 | 20 | 22.3337 | 26.3589 | 27.5143 | 89.4276 | 79.69 | 4.2 | 40 | 0.24865 | 94.2137 | 6570.424
636 | 3.3539 | 0 | 0 | 97.9542 | 96.979 | 101496.9913 | 20 | 22.3408 | 26.3569 | 27.4932 | 89.3995 | 79.743 | 4.2 | 40 | 0.24858 | 93.9744 | 6548.4879
638 | 3.3692 | 0 | 0 | 94.9353 | 90.5177 | 101495.7368 | 20 | 22.3076 | 26.3378 | 27.4882 | 89.2339 | 79.7 | 4.2 | 40 | 0.24971 | 94.7339 | 6602.5419
640 | 3.3273 | 0 | 0 | 96.9237 | 90.114 | 101505.7778 | 20 | 22.3378 | 26.3519 | 27.5003 | 89.3303 | 79.747 | 4.2 | 40 | 0.2466 | 93.1807 | 6492.3868
642 | 3.3663 | 0 | 0 | 97.0178 | 93.4835 | 101501.51 | 20 | 22.3428 | 26.383 | 27.5304 | 89.4327 | 79.623 | 4.2 | 40 | 0.24949 | 94.8863 | 6626.1134
644 | 3.3539 | 0 | 0 | 93.7324 | 88.2888 | 101502.0119 | 20 | 22.3508 | 26.3589 | 27.5264 | 89.2319 | 79.462 | 4.2 | 40 | 0.24858 | 93.7864 | 6568.688
646 | 3.3406 | 0 | 0 | 98.0711 | 92.4643 | 101496.9913 | 20 | 22.3136 | 26.3509 | 27.4962 | 89.1033 | 79.39 | 4.2 | 40 | 0.24759 | 94.0926 | 6594.1577
648 | 3.3544 | 0 | 0 | 93.6361 | 91.3525 | 101498.4968 | 20 | 22.3187 | 26.3318 | 27.4752 | 89.1485 | 79.293 | 4.2 | 40 | 0.24861 | 93.9178 | 6593.693
650 | 3.3401 | 0 | 0 | 94.4807 | 89.8825 | 101501.7609 | 20 | 22.3327 | 26.372 | 27.5153 | 89.2158 | 79.353 | 4.2 | 40 | 0.24755 | 94.1255 | 6602.9502
652 | 3.3796 | 0 | 0 | 100.3433 | 94.9406 | 101495.4836 | 20 | 22.3358 | 26.3449 | 27.5103 | 89.2399 | 79.353 | 4.2 | 40 | 0.25048 | 94.528 | 6631.5353
654 | 3.3342 | 0 | 0 | 94.2447 | 87.6953 | 101497.2422 | 20 | 22.3277 | 26.3077 | 27.4832 | 89.1535 | 79.29 | 4.2 | 40 | 0.24711 | 92.58 | 6501.1471
656 | 3.3919 | 0 | 0 | 94.4154 | 89.8992 | 101509.042 | 20 | 22.3056 | 26.3047 | 27.4591 | 89.4005 | 79.356 | 4.2 | 40 | 0.25139 | 94.6356 | 6635.227
658 | 3.3154 | 0 | 0 | 99.5282 | 97.206 | 101496.9913 | 20 | 22.2915 | 26.3208 | 27.4511 | 89.5993 | 79.395 | 4.2 | 40 | 0.24572 | 93.1976 | 6528.3371
660 | 3.2873 | 0 | 0 | 94.9353 | 88.9149 | 101496.7404 | 20 | 22.3056 | 26.3238 | 27.4591 | 89.6937 | 79.329 | 4.2 | 40 | 0.24364 | 92.1532 | 6464.2408
662 | 3.3796 | 0 | 0 | 95.5607 | 88.9286 | 101494.9818 | 20 | 22.3358 | 26.3268 | 27.4852 | 89.7549 | 79.352 | 4.2 | 40 | 0.25048 | 94.1017 | 6601.746
664 | 3.4067 | 0 | 0 | 98.0339 | 95.3611 | 101504.5233 | 20 | 22.3297 | 26.3157 | 27.4802 | 89.7118 | 79.22 | 4.2 | 40 | 0.25249 | 94.7383 | 6661.1269
666 | 3.3134 | 0 | 0 | 94.2234 | 90.646 | 101503.0178 | 20 | 22.3026 | 26.2916 | 27.4531 | 89.7088 | 78.985 | 4.2 | 40 | 0.24558 | 92.2133 | 6507.3692
668 | 3.3801 | 0 | 0 | 97.8359 | 90.0525 | 101499.5027 | 20 | 22.3277 | 26.2866 | 27.44 | 89.5863 | 78.812 | 4.2 | 40 | 0.25052 | 93.3575 | 6611.2185
670 | 3.3806 | 0 | 0 | 93.8106 | 91.7396 | 101497.7441 | 20 | 22.3719 | 26.3348 | 27.4872 | 89.4236 | 78.65 | 4.2 | 40 | 0.25055 | 93.4657 | 6643.1359
672 | 3.3381 | 0 | 0 | 94.7289 | 89.2579 | 101504.0214 | 20 | 22.3739 | 26.3187 | 27.4822 | 89.2489 | 78.584 | 4.2 | 40 | 0.24741 | 91.8708 | 6537.6776
674 | 3.3549 | 0 | 0 | 100.3827 | 97.0542 | 101496.7404 | 20 | 22.3518 | 26.3027 | 27.436 | 89.0351 | 78.515 | 4.2 | 40 | 0.24865 | 92.474 | 6586.0933
676 | 3.3668 | 0 | 0 | 94.4913 | 88.666 | 101498.4968 | 20 | 22.3026 | 26.2916 | 27.4229 | 88.774 | 78.509 | 4.2 | 40 | 0.24953 | 93.6973 | 6668.0859
678 | 3.3485 | 0 | 0 | 96.9441 | 89.0075 | 101501.7609 | 20 | 22.382 | 26.3127 | 27.4491 | 88.6827 | 78.52 | 4.2 | 40 | 0.24818 | 91.8275 | 6542.9815
680 | 3.3529 | 0 | 0 | 97.2932 | 95.6039 | 101495.9877 | 20 | 22.385 | 26.3378 | 27.4691 | 88.77 | 78.488 | 4.2 | 40 | 0.24851 | 92.4664 | 6592.6119
682 | 3.3396 | 0 | 0 | 93.6672 | 90.668 | 101498.7477 | 20 | 22.3659 | 26.3157 | 27.4862 | 88.8202 | 78.62 | 4.2 | 40 | 0.24752 | 92.0286 | 6543.7773
684 | 3.3544 | 0 | 0 | 99.1313 | 90.6991 | 101494.229 | 20 | 22.3307 | 26.3057 | 27.4541 | 88.7841 | 78.696 | 4.2 | 40 | 0.24861 | 93.0245 | 6601.5497
686 | 3.384 | 0 | 0 | 94.2621 | 90.7355 | 101500.2555 | 20 | 22.3689 | 26.3187 | 27.4651 | 88.8252 | 78.852 | 4.2 | 40 | 0.25081 | 93.253 | 6603.9577
688 | 3.3539 | 0 | 0 | 94.587 | 89.053 | 101501.51 | 20 | 22.391 | 26.3429 | 27.4862 | 88.8252 | 78.82 | 4.2 | 40 | 0.24858 | 92.4701 | 6554.7913
690 | 3.3282 | 0 | 0 | 100.2052 | 97.319 | 101496.9913 | 20 | 22.3659 | 26.3378 | 27.4892 | 88.8654 | 78.806 | 4.2 | 40 | 0.24668 | 92.2287 | 6536.3971
692 | 3.4334 | 0 | 0 | 95.8817 | 88.2152 | 101496.2386 | 20 | 22.2976 | 26.3077 | 27.4621 | 88.77 | 78.713 | 4.2 | 40 | 0.25447 | 96.0574 | 6810.7181
694 | 3.3549 | 0 | 0 | 96.9692 | 88.8048 | 101504.7742 | 20 | 22.3277 | 26.2997 | 27.4621 | 88.6405 | 78.664 | 4.2 | 40 | 0.24865 | 92.9678 | 6600.9166
696 | 3.351 | 0 | 0 | 97.7205 | 95.1964 | 101502.5137 | 20 | 22.3468 | 26.3137 | 27.4651 | 88.4096 | 78.725 | 4.2 | 40 | 0.24836 | 92.7408 | 6579.9056
698 | 3.3406 | 0 | 0 | 93.9722 | 90.6331 | 101497.7441 | 20 | 22.3498 | 26.2997 | 27.4541 | 88.3765 | 78.886 | 4.2 | 40 | 0.24759 | 92.0559 | 6513.0597
700 | 3.3544 | 0 | 0 | 100.4768 | 90.4137 | 101498.7477 | 20 | 22.3056 | 26.2977 | 27.427 | 88.765 | 79.144 | 4.2 | 40 | 0.24861 | 93.4242 | 6574.7291
702 | 3.3539 | 0 | 0 | 95.4605 | 92.1137 | 101505.7778 | 20 | 22.3217 | 26.2705 | 27.4511 | 89.0793 | 79.254 | 4.2 | 40 | 0.24858 | 92.3999 | 6491.9118
704 | 3.3539 | 0 | 0 | 94.1855 | 89.903 | 101496.7404 | 20 | 22.3167 | 26.2916 | 27.4701 | 89.3935 | 79.33 | 4.2 | 40 | 0.24858 | 93.011 | 6525.5588
706 | 3.3939 | 0 | 0 | 99.6853 | 95.8718 | 101498.9986 | 20 | 22.3358 | 26.3268 | 27.4782 | 89.279 | 79.469 | 4.2 | 40 | 0.25154 | 94.5003 | 6616.132
708 | 3.3811 | 0 | 0 | 94.8435 | 90.7591 | 101500.0046 | 20 | 22.3508 | 26.3509 | 27.4872 | 89.4738 | 79.599 | 4.2 | 40 | 0.25059 | 94.356 | 6592.7719
710 | 3.3534 | 0 | 0 | 96.4873 | 88.8914 | 101507.7874 | 20 | 22.3187 | 26.3519 | 27.5113 | 89.7319 | 79.582 | 4.2 | 40 | 0.24854 | 94.3601 | 6591.3128
712 | 3.3287 | 0 | 0 | 100.8123 | 97.058 | 101493.9781 | 20 | 22.3327 | 26.3398 | 27.4962 | 89.6465 | 79.517 | 4.2 | 40 | 0.24671 | 93.059 | 6509.4164
714 | 3.3949 | 0 | 0 | 93.4228 | 88.905 | 101494.7308 | 20 | 22.3478 | 26.3338 | 27.4902 | 89.53 | 79.454 | 4.2 | 40 | 0.25161 | 94.4088 | 6612.8573
716 | 3.3608 | 0 | 0 | 94.8344 | 91.4011 | 101501.0082 | 20 | 22.397 | 26.374 | 27.5344 | 89.524 | 79.518 | 4.2 | 40 | 0.24909 | 93.2493 | 6529.9526
718 | 3.3534 | 0 | 0 | 99.9183 | 94.9315 | 101505.276 | 20 | 22.3729 | 26.386 | 27.5214 | 89.6084 | 79.606 | 4.2 | 40 | 0.24854 | 93.8899 | 6561.9324
720 | 3.3406 | 0 | 0 | 94.7448 | 89.2898 | 101499.2518 | 20 | 22.3287 | 26.3599 | 27.5334 | 89.4377 | 79.597 | 4.2 | 40 | 0.24759 | 93.9521 | 6562.2428
722 | 3.3011 | 0 | 0 | 96.9381 | 90.6725 | 101499.5027 | 20 | 22.3478 | 26.4011 | 27.5113 | 89.4999 | 79.505 | 4.2 | 40 | 0.24466 | 93.3502 | 6532.8722
724 | 3.351 | 0 | 0 | 96.0524 | 89.7163 | 101502.2628 | 20 | 22.392 | 26.381 | 27.5434 | 89.5361 | 79.532 | 4.2 | 40 | 0.24836 | 93.2572 | 6528.3304
726 | 3.3327 | 0 | 0 | 94.3737 | 89.1722 | 101504.5233 | 20 | 22.386 | 26.4101 | 27.5404 | 89.6274 | 79.464 | 4.2 | 40 | 0.24701 | 93.5663 | 6557.0779
728 | 3.3268 | 0 | 0 | 100.8745 | 97.7911 | 101500.0046 | 20 | 22.3528 | 26.376 | 27.5193 | 89.6485 | 79.501 | 4.2 | 40 | 0.24657 | 93.3767 | 6535.7625
730 | 3.3682 | 0 | 0 | 94.587 | 89.3725 | 101494.4799 | 20 | 22.3448 | 26.3378 | 27.5053 | 89.6415 | 79.518 | 4.2 | 40 | 0.24964 | 93.8327 | 6564.7993
732 | 3.4058 | 0 | 0 | 94.5885 | 90.054 | 101502.0119 | 20 | 22.381 | 26.3921 | 27.5294 | 89.5551 | 79.518 | 4.2 | 40 | 0.25242 | 95.3074 | 6672.1962
734 | 3.3268 | 0 | 0 | 98.8133 | 97.3539 | 101497.4932 | 20 | 22.389 | 26.386 | 27.5193 | 89.6104 | 79.518 | 4.2 | 40 | 0.24657 | 92.7704 | 6495.5055
736 | 3.3534 | 0 | 0 | 95.3193 | 89.437 | 101496.2386 | 20 | 22.3589 | 26.4001 | 27.5324 | 89.4427 | 79.688 | 4.2 | 40 | 0.24854 | 94.5479 | 6596.8492
738 | 3.3672 | 0 | 0 | 97.7122 | 90.3712 | 101496.4895 | 20 | 22.3277 | 26.3619 | 27.5113 | 89.5431 | 79.779 | 4.2 | 40 | 0.24957 | 94.7726 | 6598.4696
740 | 3.3001 | 0 | 0 | 95.0233 | 93.224 | 101500.0046 | 20 | 22.3609 | 26.37 | 27.5113 | 89.6947 | 79.866 | 4.2 | 40 | 0.24459 | 92.3047 | 6420.621
742 | 3.3268 | 0 | 0 | 93.5503 | 90.2232 | 101498.2459 | 20 | 22.3779 | 26.3941 | 27.5244 | 89.9899 | 79.848 | 4.2 | 40 | 0.24657 | 93.2134 | 6487.7903
744 | 3.3539 | 0 | 0 | 100.8753 | 96.2399 | 101498.7477 | 20 | 22.3609 | 26.382 | 27.5454 | 90.0973 | 79.798 | 4.2 | 40 | 0.24858 | 94.0919 | 6552.685
746 | 3.3386 | 0 | 0 | 94.637 | 89.4992 | 101505.0251 | 20 | 22.3136 | 26.3589 | 27.5183 | 89.9216 | 79.701 | 4.2 | 40 | 0.24744 | 94.2241 | 6567.5891
748 | 3.3934 | 0 | 0 | 94.1878 | 89.7262 | 101502.2628 | 20 | 22.382 | 26.38 | 27.5294 | 89.7409 | 79.755 | 4.2 | 40 | 0.2515 | 94.6528 | 6599.1155
750 | 3.3534 | 0 | 0 | 98.7587 | 96.9335 | 101498.9986 | 20 | 22.3719 | 26.4011 | 27.5374 | 89.6043 | 79.768 | 4.2 | 40 | 0.24854 | 94.2659 | 6569.4993
752 | 3.3924 | 0 | 0 | 94.7509 | 89.6199 | 101499.7536 | 20 | 22.3478 | 26.3881 | 27.5434 | 89.6827 | 79.88 | 4.2 | 40 | 0.25143 | 95.6239 | 6648.3722
754 | 3.3811 | 0 | 0 | 97.6431 | 89.2435 | 101502.7669 | 20 | 22.3538 | 26.38 | 27.5274 | 89.8383 | 79.853 | 4.2 | 40 | 0.25059 | 94.972 | 6606.8462
756 | 3.4063 | 0 | 0 | 96.2543 | 94.1612 | 101503.2687 | 20 | 22.3347 | 26.367 | 27.5304 | 89.9658 | 79.826 | 4.2 | 40 | 0.25246 | 95.8226 | 6666.9348
758 | 3.3801 | 0 | 0 | 93.9654 | 89.0887 | 101500.2555 | 20 | 22.3759 | 26.4011 | 27.5404 | 90.2339 | 79.949 | 4.2 | 40 | 0.25052 | 94.9205 | 6594.7855
760 | 3.3598 | 0 | 0 | 100.1566 | 94.5445 | 101499.2518 | 20 | 22.39 | 26.3971 | 27.5324 | 90.3985 | 80.001 | 4.2 | 40 | 0.24902 | 93.9282 | 6521.5491
762 | 3.3663 | 0 | 0 | 94.9907 | 88.6144 | 101504.5233 | 20 | 22.387 | 26.4071 | 27.5485 | 90.5672 | 80.061 | 4.2 | 40 | 0.24949 | 94.4143 | 6548.1361
764 | 3.3534 | 0 | 0 | 95.0863 | 88.3298 | 101502.2628 | 20 | 22.3749 | 26.384 | 27.5344 | 90.8202 | 80.127 | 4.2 | 40 | 0.24854 | 93.7959 | 6496.4525
766 | 3.3411 | 0 | 0 | 100.7751 | 98.5151 | 101498.9986 | 20 | 22.3589 | 26.385 | 27.5465 | 90.7298 | 80.031 | 4.2 | 40 | 0.24763 | 93.8487 | 6509.1194
768 | 3.3411 | 0 | 0 | 93.6004 | 90.1307 | 101494.7308 | 20 | 22.389 | 26.4242 | 27.5515 | 90.7298 | 79.989 | 4.2 | 40 | 0.24763 | 94.0593 | 6531.8943
770 | 3.4043 | 0 | 0 | 94.9581 | 88.7957 | 101502.2628 | 20 | 22.395 | 26.4212 | 27.5595 | 90.6023 | 79.986 | 4.2 | 40 | 0.25231 | 95.6236 | 6641.5699
772 | 3.3401 | 0 | 0 | 98.896 | 95.3466 | 101504.2724 | 20 | 22.3538 | 26.4031 | 27.5324 | 90.4849 | 79.986 | 4.2 | 40 | 0.24755 | 94.3594 | 6549.0819
774 | 3.3811 | 0 | 0 | 95.506 | 90.035 | 101496.4895 | 20 | 22.3508 | 26.373 | 27.5575 | 90.4658 | 79.969 | 4.2 | 40 | 0.25059 | 94.8773 | 6586.6212
776 | 3.3544 | 0 | 0 | 97.4321 | 93.4266 | 101499.7536 | 20 | 22.395 | 26.4112 | 27.5274 | 90.4126 | 80.031 | 4.2 | 40 | 0.24861 | 93.988 | 6522.8679
778 | 3.3806 | 0 | 0 | 97.4018 | 91.2318 | 101510.2988 | 20 | 22.382 | 26.4353 | 27.5525 | 90.2931 | 80.058 | 4.2 | 40 | 0.25055 | 95.5977 | 6629.9768
780 | 3.3796 | 0 | 0 | 94.6689 | 88.4497 | 101506.2797 | 20 | 22.39 | 26.4051 | 27.5595 | 90.5471 | 80.123 | 4.2 | 40 | 0.25048 | 94.6698 | 6559.1472
782 | 3.3658 | 0 | 0 | 99.6284 | 93.4054 | 101503.5196 | 20 | 22.3709 | 26.3971 | 27.5615 | 90.6947 | 80.207 | 4.2 | 40 | 0.24946 | 94.5421 | 6538.6249
784 | 3.3796 | 0 | 0 | 93.6254 | 91.3639 | 101504.5233 | 20 | 22.3779 | 26.4051 | 27.5685 | 90.6907 | 80.097 | 4.2 | 40 | 0.25048 | 94.9541 | 6580.4301
786 | 3.3144 | 0 | 0 | 94.5202 | 90.1345 | 101504.7742 | 20 | 22.4262 | 26.4373 | 27.5655 | 90.3744 | 79.948 | 4.2 | 40 | 0.24565 | 92.7512 | 6449.8084
788 | 3.3663 | 0 | 0 | 99.4888 | 96.0228 | 101503.0178 | 20 | 22.3789 | 26.4021 | 27.5685 | 90.0692 | 79.775 | 4.2 | 40 | 0.24949 | 94.4851 | 6584.7824
790 | 3.3396 | 0 | 0 | 94.1043 | 87.6748 | 101492.2217 | 20 | 22.3629 | 26.373 | 27.5224 | 89.8604 | 79.636 | 4.2 | 40 | 0.24752 | 93.4327 | 6525.4143
792 | 3.3529 | 0 | 0 | 96.1792 | 90.8061 | 101505.0251 | 20 | 22.393 | 26.3941 | 27.5384 | 89.512 | 79.59 | 4.2 | 40 | 0.24851 | 93.5941 | 6545.3867
794 | 3.3396 | 0 | 0 | 97.9952 | 94.6674 | 101506.0287 | 20 | 22.3679 | 26.4101 | 27.5304 | 89.3564 | 79.539 | 4.2 | 40 | 0.24752 | 94.1816 | 6589.4516
796 | 3.3544 | 0 | 0 | 94.6833 | 89.0507 | 101496.4895 | 20 | 22.3769 | 26.3961 | 27.5294 | 89.0602 | 79.485 | 4.2 | 40 | 0.24861 | 94.0586 | 6588.1115
798 | 3.3534 | 0 | 0 | 98.9659 | 91.6333 | 101496.2386 | 20 | 22.3689 | 26.375 | 27.5294 | 88.9899 | 79.475 | 4.2 | 40 | 0.24854 | 93.7254 | 6565.0031
800 | 3.3396 | 0 | 0 | 96.1276 | 92.355 | 101507.7874 | 20 | 22.3358 | 26.3619 | 27.5063 | 89.1766 | 79.52 | 4.2 | 40 | 0.24752 | 93.8073 | 6561.756
802 | 3.3411 | 0 | 0 | 93.5708 | 90.3022 | 101500.5064 | 20 | 22.388 | 26.4001 | 27.5575 | 89.1676 | 79.453 | 4.2 | 40 | 0.24763 | 93.5208 | 6555.3873
804 | 3.3401 | 0 | 0 | 100.1209 | 97.3615 | 101497.2422 | 20 | 22.396 | 26.4132 | 27.5384 | 89.276 | 79.447 | 4.2 | 40 | 0.24755 | 93.6103 | 6563.2731
806 | 3.3648 | 0 | 0 | 94.3388 | 88.8451 | 101500.2555 | 20 | 22.386 | 26.385 | 27.5374 | 89.1807 | 79.381 | 4.2 | 40 | 0.24938 | 93.8777 | 6588.4842
808 | 3.3628 | 0 | 0 | 95.5424 | 88.496 | 101503.7705 | 20 | 22.3679 | 26.368 | 27.5444 | 89.1525 | 79.458 | 4.2 | 40 | 0.24924 | 93.8462 | 6575.3066
810 | 3.3273 | 0 | 0 | 97.785 | 96.2346 | 101501.0082 | 20 | 22.387 | 26.386 | 27.5465 | 89.0351 | 79.432 | 4.2 | 40 | 0.2466 | 92.8308 | 6509.3008
812 | 3.3544 | 0 | 0 | 95.182 | 90.8903 | 101500.2555 | 20 | 22.4011 | 26.4142 | 27.5695 | 89.1415 | 79.442 | 4.2 | 40 | 0.24861 | 93.9174 | 6585.9647
814 | 3.3668 | 0 | 0 | 99.0979 | 91.7737 | 101496.2386 | 20 | 22.397 | 26.4081 | 27.5585 | 89.2288 | 79.418 | 4.2 | 40 | 0.24953 | 94.2159 | 6609.2081
816 | 3.3544 | 0 | 0 | 94.656 | 90.2817 | 101505.5269 | 20 | 22.4111 | 26.4172 | 27.5746 | 89.3092 | 79.378 | 4.2 | 40 | 0.24861 | 93.7528 | 6582.9686
818 | 3.3801 | 0 | 0 | 92.8673 | 89.374 | 101500.5064 | 20 | 22.4061 | 26.3931 | 27.5444 | 89.3062 | 79.432 | 4.2 | 40 | 0.25052 | 94.0203 | 6594.917
820 | 3.3391 | 0 | 0 | 98.6206 | 94.3714 | 101498.9986 | 20 | 22.4211 | 26.4021 | 27.5555 | 89.2198 | 79.33 | 4.2 | 40 | 0.24748 | 92.7401 | 6518.503
822 | 3.2774 | 0 | 0 | 97.0466 | 89.0507 | 101501.2591 | 20 | 22.4181 | 26.4242 | 27.5685 | 89.2158 | 79.308 | 4.2 | 40 | 0.24291 | 91.6002 | 6440.5306
824 | 3.3263 | 0 | 0 | 95.5804 | 87.6065 | 101507.2856 | 20 | 22.4181 | 26.4242 | 27.5655 | 89.1626 | 79.266 | 4.2 | 40 | 0.24653 | 92.9662 | 6541.4057
826 | 3.3579 | 0 | 0 | 98.9659 | 97.2348 | 101494.7308 | 20 | 22.3769 | 26.3619 | 27.5414 | 89.1435 | 79.21 | 4.2 | 40 | 0.24887 | 93.3554 | 6570.5012
828 | 3.3534 | 0 | 0 | 94.4154 | 90.4585 | 101501.2591 | 20 | 22.382 | 26.368 | 27.5254 | 89.2389 | 79.208 | 4.2 | 40 | 0.24854 | 93.2554 | 6564.2721
830 | 3.3287 | 0 | 0 | 94.5778 | 90.1314 | 101507.0347 | 20 | 22.4041 | 26.3971 | 27.5605 | 89.1917 | 79.21 | 4.2 | 40 | 0.24671 | 92.7322 | 6529.751
832 | 3.3549 | 0 | 0 | 99.1192 | 95.1341 | 101503.7705 | 20 | 22.4101 | 26.3971 | 27.5444 | 89.1315 | 79.003 | 4.2 | 40 | 0.24865 | 93.32 | 6595.8818
834 | 3.3791 | 0 | 0 | 94.9368 | 89.1039 | 101501.2591 | 20 | 22.3599 | 26.3489 | 27.5153 | 88.8795 | 78.696 | 4.2 | 40 | 0.25044 | 94.0404 | 6677.0934
836 | 3.3939 | 0 | 0 | 97.0678 | 91.1066 | 101499.2518 | 20 | 22.3659 | 26.3378 | 27.5043 | 88.6174 | 78.725 | 4.2 | 40 | 0.25154 | 94.0483 | 6674.9295
838 | 3.3347 | 0 | 0 | 94.0686 | 93.158 | 101499.2518 | 20 | 22.4101 | 26.3599 | 27.5173 | 88.5652 | 78.74 | 4.2 | 40 | 0.24715 | 91.8923 | 6525.2939
840 | 3.3554 | 0 | 0 | 93.1314 | 89.928 | 101498.4968 | 20 | 22.393 | 26.373 | 27.5073 | 88.8453 | 78.684 | 4.2 | 40 | 0.24869 | 93.1692 | 6620.5412
842 | 3.3282 | 0 | 0 | 101.9795 | 94.9497 | 101490.2121 | 20 | 22.3709 | 26.3358 | 27.4962 | 89.014 | 78.538 | 4.2 | 40 | 0.24668 | 92.0655 | 6556.5418
844 | 3.3396 | 0 | 0 | 95.0385 | 91.2736 | 101502.7669 | 20 | 22.3327 | 26.3007 | 27.4591 | 88.7981 | 78.457 | 4.2 | 40 | 0.24752 | 92.45 | 6588.9493
846 | 3.3307 | 0 | 0 | 93.7605 | 90.1223 | 101500.7573 | 20 | 22.394 | 26.3509 | 27.4952 | 88.7048 | 78.451 | 4.2 | 40 | 0.24686 | 91.947 | 6560.9673
848 | 3.3134 | 0 | 0 | 99.3309 | 95.5106 | 101502.5137 | 20 | 22.3719 | 26.3308 | 27.4721 | 88.4688 | 78.453 | 4.2 | 40 | 0.24558 | 91.5165 | 6527.4384
850 | 3.3411 | 0 | 0 | 94.2174 | 87.1891 | 101497.2422 | 20 | 22.3739 | 26.3198 | 27.4872 | 88.6315 | 78.648 | 4.2 | 40 | 0.24763 | 91.9757 | 6537.6942
852 | 3.3682 | 0 | 0 | 95.8119 | 91.3806 | 101501.0082 | 20 | 22.3659 | 26.3228 | 27.4641 | 88.7118 | 78.72 | 4.2 | 40 | 0.24964 | 92.9829 | 6599.8998
854 | 3.3381 | 0 | 0 | 99.0486 | 95.1349 | 101507.2856 | 20 | 22.38 | 26.3418 | 27.4882 | 88.9126 | 78.753 | 4.2 | 40 | 0.24741 | 92.2685 | 6546.9913
856 | 3.3406 | 0 | 0 | 95.4802 | 89.3596 | 101496.2386 | 20 | 22.4201 | 26.387 | 27.5254 | 88.9859 | 78.699 | 4.2 | 40 | 0.24759 | 92.4535 | 6571.1
858 | 3.3401 | 0 | 0 | 97.9937 | 90.6088 | 101493.7272 | 20 | 22.4101 | 26.3921 | 27.5083 | 88.8272 | 78.527 | 4.2 | 40 | 0.24755 | 92.791 | 6614.1227
860 | 3.3297 | 0 | 0 | 92.9652 | 93.1101 | 101501.2591 | 20 | 22.4252 | 26.3559 | 27.5033 | 88.8202 | 78.462 | 4.2 | 40 | 0.24679 | 91.3129 | 6518.0656
862 | 3.3347 | 0 | 0 | 94.0679 | 89.2708 | 101501.0082 | 20 | 22.3789 | 26.3288 | 27.4711 | 88.7379 | 78.359 | 4.2 | 40 | 0.24715 | 91.8924 | 6566.0852
864 | 3.3134 | 0 | 0 | 99.8128 | 95.3891 | 101500.2555 | 20 | 22.4211 | 26.3388 | 27.4892 | 88.7961 | 78.421 | 4.2 | 40 | 0.24558 | 90.5643 | 6468.8929
866 | 3.3411 | 0 | 0 | 94.2136 | 87.6581 | 101498.2459 | 20 | 22.4242 | 26.3439 | 27.4942 | 88.8534 | 78.433 | 4.2 | 40 | 0.24763 | 91.3667 | 6525.1639
868 | 3.3263 | 0 | 0 | 93.718 | 90.5898 | 101503.7705 | 20 | 22.4131 | 26.3489 | 27.4993 | 88.8463 | 78.448 | 4.2 | 40 | 0.24653 | 91.3347 | 6519.8433
870 | 3.3455 | 0 | 0 | 96.9449 | 88.7775 | 101500.0046 | 20 | 22.38 | 26.3167 | 27.4651 | 88.9758 | 78.465 | 4.2 | 40 | 0.24796 | 91.8871 | 6553.4096
872 | 3.3273 | 0 | 0 | 93.7021 | 92.1585 | 101505.7778 | 20 | 22.3609 | 26.2846 | 27.4591 | 88.9467 | 78.482 | 4.2 | 40 | 0.2466 | 91.0823 | 6491.8333
874 | 3.3544 | 0 | 0 | 94.1688 | 89.1866 | 101506.0287 | 20 | 22.3719 | 26.2846 | 27.4561 | 88.8102 | 78.465 | 4.2 | 40 | 0.24861 | 91.567 | 6529.6462
876 | 3.3539 | 0 | 0 | 94.4913 | 89.6267 | 101504.0214 | 20 | 22.4181 | 26.3278 | 27.4651 | 88.6325 | 78.482 | 4.2 | 40 | 0.24858 | 91.4829 | 6527.0452
878 | 3.3529 | 0 | 0 | 100.3357 | 97.5209 | 101499.2518 | 20 | 22.4051 | 26.3439 | 27.4732 | 88.4909 | 78.507 | 4.2 | 40 | 0.24851 | 92.1373 | 6569.281
880 | 3.3801 | 0 | 0 | 93.5275 | 88.8307 | 101495.9877 | 20 | 22.3629 | 26.2906 | 27.4732 | 88.3112 | 78.546 | 4.2 | 40 | 0.25052 | 92.6231 | 6594.3697
882 | 3.3682 | 0 | 0 | 95.6464 | 88.7115 | 101505.276 | 20 | 22.3739 | 26.3117 | 27.4621 | 88.1787 | 78.592 | 4.2 | 40 | 0.24964 | 92.5344 | 6583.9599
884 | 3.3134 | 0 | 0 | 97.0534 | 95.2495 | 101504.5233 | 20 | 22.3538 | 26.3027 | 27.4551 | 88.1686 | 78.62 | 4.2 | 40 | 0.24558 | 91.2844 | 6489.4667
886 | 3.3549 | 0 | 0 | 94.2166 | 89.7474 | 101499.7536 | 20 | 22.3589 | 26.3047 | 27.4541 | 88.1887 | 78.706 | 4.2 | 40 | 0.24865 | 92.3564 | 6556.2437
888 | 3.3268 | 0 | 0 | 98.0605 | 91.7206 | 101500.0046 | 20 | 22.4242 | 26.3609 | 27.4973 | 88.3795 | 78.771 | 4.2 | 40 | 0.24657 | 91.3716 | 6486.3662
890 | 3.3534 | 0 | 0 | 96.0752 | 91.5529 | 101503.0178 | 20 | 22.392 | 26.3589 | 27.5033 | 88.3323 | 78.649 | 4.2 | 40 | 0.24854 | 92.8089 | 6598.9217
892 | 3.3139 | 0 | 0 | 94.0975 | 89.9129 | 101502.0119 | 20 | 22.3679 | 26.3338 | 27.4742 | 88.1455 | 78.909 | 4.2 | 40 | 0.24561 | 91.6927 | 6486.8017
894 | 3.3811 | 0 | 0 | 100.6415 | 95.4157 | 101492.9745 | 20 | 22.4 | 26.3599 | 27.4872 | 88.2429 | 79.08 | 4.2 | 40 | 0.25059 | 93.4081 | 6591.9687
896 | 3.3806 | 0 | 0 | 94.3062 | 87.1671 | 101498.7477 | 20 | 22.4201 | 26.4001 | 27.5173 | 88.259 | 79.074 | 4.2 | 40 | 0.25055 | 93.8682 | 6627.4898
898 | 3.3534 | 0 | 0 | 94.7357 | 89.3034 | 101504.5233 | 20 | 22.4292 | 26.4112 | 27.5485 | 88.3263 | 79.112 | 4.2 | 40 | 0.24854 | 93.1612 | 6574.209
900 | 3.3401 | 0 | 0 | 98.6661 | 96.5252 | 101498.7477 | 20 | 22.4021 | 26.4142 | 27.5645 | 88.4608 | 79.129 | 4.2 | 40 | 0.24755 | 93.4932 | 6592.509
902 | 3.3534 | 0 | 0 | 95.4832 | 88.8405 | 101493.4763 | 20 | 22.3558 | 26.379 | 27.5404 | 88.5441 | 79.233 | 4.2 | 40 | 0.24854 | 94.125 | 6619.5267
904 | 3.3263 | 0 | 0 | 96.2171 | 88.7009 | 101500.7573 | 20 | 22.4131 | 26.3901 | 27.5354 | 88.6766 | 79.302 | 4.2 | 40 | 0.24653 | 92.2903 | 6489.163
906 | 3.3139 | 0 | 0 | 94.8458 | 94.8549 | 101504.7742 | 20 | 22.4191 | 26.4112 | 27.5535 | 88.6184 | 79.236 | 4.2 | 40 | 0.24561 | 92.2963 | 6497.8072
908 | 3.3682 | 0 | 0 | 94.1901 | 89.6047 | 101500.5064 | 20 | 22.4191 | 26.4332 | 27.5806 | 88.6766 | 79.192 | 4.2 | 40 | 0.24964 | 94.328 | 6645.989
910 | 3.3386 | 0 | 0 | 99.5404 | 91.6204 | 101496.7404 | 20 | 22.3669 | 26.377 | 27.5294 | 88.8684 | 79.168 | 4.2 | 40 | 0.24744 | 93.4051 | 6577.6934
912 | 3.3406 | 0 | 0 | 93.0312 | 92.2609 | 101500.7573 | 20 | 22.4131 | 26.3951 | 27.5324 | 89.0873 | 79.172 | 4.2 | 40 | 0.24759 | 92.8047 | 6540.2734
914 | 3.3663 | 0 | 0 | 95.4423 | 90.202 | 101502.7669 | 20 | 22.394 | 26.4061 | 27.5515 | 89.1325 | 79.038 | 4.2 | 40 | 0.24949 | 94.2256 | 6653.8812
916 | 3.3203 | 0 | 0 | 102.2231 | 94.7646 | 101494.9818 | 20 | 22.386 | 26.3951 | 27.5454 | 89.1616 | 78.902 | 4.2 | 40 | 0.24609 | 92.8707 | 6573.0527
918 | 3.3801 | 0 | 0 | 93.9965 | 88.6986 | 101496.2386 | 20 | 22.3558 | 26.3499 | 27.5133 | 89.017 | 78.778 | 4.2 | 40 | 0.25052 | 94.1863 | 6677.2597
920 | 3.3401 | 0 | 0 | 94.8427 | 90.1656 | 101502.5137 | 20 | 22.3719 | 26.3599 | 27.5053 | 88.9527 | 78.83 | 4.2 | 40 | 0.24755 | 92.9316 | 6584.1157
922 | 3.3747 | 0 | 0 | 99.1548 | 95.6616 | 101504.5233 | 20 | 22.4051 | 26.3981 | 27.5214 | 89.0843 | 78.936 | 4.2 | 40 | 0.25011 | 94.0112 | 6652.0157
924 | 3.3534 | 0 | 0 | 93.7218 | 88.7388 | 101500.7573 | 20 | 22.394 | 26.3639 | 27.5434 | 89.2529 | 79.012 | 4.2 | 40 | 0.24854 | 92.8794 | 6561.8275
926 | 3.3258 | 0 | 0 | 98.3026 | 90.416 | 101496.2386 | 20 | 22.383 | 26.3911 | 27.5193 | 89.2529 | 79.105 | 4.2 | 40 | 0.24649 | 92.9993 | 6558.2474
928 | 3.3554 | 0 | 0 | 93.5806 | 91.3518 | 101498.9986 | 20 | 22.382 | 26.369 | 27.4922 | 89.2941 | 79.113 | 4.2 | 40 | 0.24869 | 93.3338 | 6580.7955
930 | 3.4063 | 0 | 0 | 94.1369 | 89.2071 | 101501.51 | 20 | 22.4101 | 26.4041 | 27.5224 | 89.4618 | 79.125 | 4.2 | 40 | 0.25246 | 94.9152 | 6694.2002
932 | 3.3292 | 0 | 0 | 101.2358 | 95.4719 | 101489.9612 | 20 | 22.399 | 26.3911 | 27.5404 | 89.3955 | 79.2 | 4.2 | 40 | 0.24675 | 92.7225 | 6529.6463
934 | 3.3199 | 0 | 0 | 94.3654 | 87.155 | 101497.7441 | 20 | 22.391 | 26.3991 | 27.5354 | 89.3714 | 79.159 | 4.2 | 40 | 0.24605 | 92.8335 | 6541.2582
936 | 3.3663 | 0 | 0 | 95.1372 | 89.4029 | 101506.2797 | 20 | 22.3769 | 26.3881 | 27.5214 | 88.9688 | 79.177 | 4.2 | 40 | 0.24949 | 94.2021 | 6633.9417
938 | 3.3406 | 0 | 0 | 98.424 | 95.5417 | 101502.7669 | 20 | 22.3709 | 26.381 | 27.5254 | 88.7941 | 79.25 | 4.2 | 40 | 0.24759 | 93.4603 | 6572.5605
940 | 3.3292 | 0 | 0 | 94.6014 | 89.0697 | 101495.4836 | 20 | 22.3789 | 26.38 | 27.5133 | 88.7519 | 79.273 | 4.2 | 40 | 0.24675 | 92.9326 | 6533.7305
942 | 3.3549 | 0 | 0 | 96.4023 | 89.5622 | 101494.9818 | 20 | 22.4161 | 26.4212 | 27.5625 | 88.8985 | 79.228 | 4.2 | 40 | 0.24865 | 93.7432 | 6600.251
944 | 3.3668 | 0 | 0 | 93.2627 | 93.5807 | 101501.0082 | 20 | 22.4091 | 26.4182 | 27.5465 | 89.1164 | 79.189 | 4.2 | 40 | 0.24953 | 94.1686 | 6633.9391
946 | 3.3411 | 0 | 0 | 93.8197 | 90.4555 | 101504.5233 | 20 | 22.3739 | 26.3921 | 27.5234 | 89.267 | 79.245 | 4.2 | 40 | 0.24763 | 93.6613 | 6587.6265
948 | 3.3011 | 0 | 0 | 100.5854 | 92.0788 | 101497.7441 | 20 | 22.3689 | 26.387 | 27.5133 | 89.0893 | 79.162 | 4.2 | 40 | 0.24466 | 92.5404 | 6517.7248
950 | 3.3534 | 0 | 0 | 93.9001 | 88.5764 | 101501.7609 | 20 | 22.4151 | 26.4112 | 27.5716 | 88.9146 | 79.03 | 4.2 | 40 | 0.24854 | 93.4902 | 6605.3459
952 | 3.3396 | 0 | 0 | 94.0405 | 88.9111 | 101501.51 | 20 | 22.4372 | 26.4212 | 27.5635 | 88.9768 | 78.957 | 4.2 | 40 | 0.24752 | 92.8239 | 6569.3049
954 | 3.3144 | 0 | 0 | 100.7964 | 97.2113 | 101497.4932 | 20 | 22.393 | 26.4051 | 27.5585 | 88.8905 | 79.03 | 4.2 | 40 | 0.24565 | 92.7746 | 6552.2258
956 | 3.3149 | 0 | 0 | 94.2356 | 88.5567 | 101500.7573 | 20 | 22.3488 | 26.379 | 27.5183 | 88.9849 | 79.141 | 4.2 | 40 | 0.24569 | 93.2068 | 6564.7613
958 | 3.3144 | 0 | 0 | 94.6985 | 88.5772 | 101500.0046 | 20 | 22.4272 | 26.4162 | 27.5465 | 89.3212 | 79.228 | 4.2 | 40 | 0.24565 | 92.2402 | 6495.6967
960 | 3.3401 | 0 | 0 | 98.9507 | 97.1286 | 101495.7368 | 20 | 22.4201 | 26.4463 | 27.5766 | 89.4246 | 79.236 | 4.2 | 40 | 0.24755 | 93.8208 | 6605.255
962 | 3.3006 | 0 | 0 | 94.6575 | 89.7611 | 101497.7441 | 20 | 22.3739 | 26.4091 | 27.5695 | 89.4367 | 79.303 | 4.2 | 40 | 0.24463 | 92.9197 | 6528.8045
964 | 3.3529 | 0 | 0 | 98.1834 | 90.0973 | 101494.229 | 20 | 22.3629 | 26.4041 | 27.5575 | 89.5943 | 79.403 | 4.2 | 40 | 0.24851 | 94.534 | 6629.3017
966 | 3.3263 | 0 | 0 | 94.6849 | 91.0634 | 101502.7669 | 20 | 22.4021 | 26.4041 | 27.5605 | 89.7248 | 79.442 | 4.2 | 40 | 0.24653 | 92.8731 | 6512.8456
968 | 3.3144 | 0 | 0 | 93.3378 | 89.204 | 101503.7705 | 20 | 22.4242 | 26.4202 | 27.5766 | 89.7198 | 79.532 | 4.2 | 40 | 0.24565 | 92.4028 | 6472.1639
970 | 3.3668 | 0 | 0 | 100.9777 | 94.9133 | 101496.2386 | 20 | 22.399 | 26.4373 | 27.5706 | 89.8353 | 79.513 | 4.2 | 40 | 0.24953 | 94.8528 | 6643.0582
972 | 3.3544 | 0 | 0 | 94.1976 | 90.095 | 101505.276 | 20 | 22.3448 | 26.3881 | 27.5605 | 89.78 | 79.515 | 4.2 | 40 | 0.24861 | 94.6229 | 6620.4308
974 | 3.3549 | 0 | 0 | 94.99 | 88.5521 | 101502.2628 | 20 | 22.388 | 26.4071 | 27.5495 | 89.8443 | 79.505 | 4.2 | 40 | 0.24865 | 94.0724 | 6588.0498
976 | 3.3327 | 0 | 0 | 98.8847 | 96.4759 | 101500.5064 | 20 | 22.394 | 26.4182 | 27.5625 | 89.6837 | 79.469 | 4.2 | 40 | 0.24701 | 93.5662 | 6557.4242
978 | 3.3534 | 0 | 0 | 95.4696 | 89.5713 | 101500.0046 | 20 | 22.3689 | 26.3991 | 27.5495 | 89.7027 | 79.574 | 4.2 | 40 | 0.24854 | 94.2894 | 6593.0765
980 | 3.3016 | 0 | 0 | 97.1862 | 90.8752 | 101500.7573 | 20 | 22.3579 | 26.386 | 27.5625 | 89.5802 | 79.608 | 4.2 | 40 | 0.2447 | 92.7856 | 6482.8221
982 | 3.3011 | 0 | 0 | 96.6831 | 95.352 | 101504.2724 | 20 | 22.38 | 26.3961 | 27.5424 | 89.4487 | 79.544 | 4.2 | 40 | 0.24466 | 92.4941 | 6472.1891
984 | 3.3549 | 0 | 0 | 95.4089 | 89.3285 | 101504.0214 | 20 | 22.398 | 26.4383 | 27.5585 | 89.4327 | 79.658 | 4.2 | 40 | 0.24865 | 94.5661 | 6606.0866
986 | 3.3124 | 0 | 0 | 100.5831 | 93.1041 | 101495.2327 | 20 | 22.396 | 26.4132 | 27.5505 | 89.4126 | 79.688 | 4.2 | 40 | 0.2455 | 92.8353 | 6481.5595
988 | 3.3406 | 0 | 0 | 93.8592 | 88.5688 | 101506.2797 | 20 | 22.397 | 26.4353 | 27.5545 | 89.53 | 79.599 | 4.2 | 40 | 0.24759 | 94.1156 | 6581.2865
990 | 3.3672 | 0 | 0 | 95.0233 | 90.3174 | 101505.276 | 20 | 22.4011 | 26.4533 | 27.5766 | 89.6535 | 79.54 | 4.2 | 40 | 0.24957 | 95.197 | 6664.2468
992 | 3.3011 | 0 | 0 | 100.3585 | 98.0719 | 101492.9745 | 20 | 22.3709 | 26.4262 | 27.5625 | 89.5923 | 79.529 | 4.2 | 40 | 0.24466 | 93.3963 | 6536.0002
994 | 3.3682 | 0 | 0 | 93.8751 | 88.1158 | 101497.4932 | 20 | 22.4312 | 26.4312 | 27.5816 | 89.5451 | 79.386 | 4.2 | 40 | 0.24964 | 93.9975 | 6601.5473
996 | 3.3564 | 0 | 0 | 95.6844 | 90.01 | 101500.7573 | 20 | 22.4252 | 26.4523 | 27.5786 | 89.5752 | 79.339 | 4.2 | 40 | 0.24876 | 94.3019 | 6627.6947
998 | 3.3717 | 0 | 0 | 99.6527 | 97.3904 | 101499.7536 | 20 | 22.4011 | 26.4302 | 27.5977 | 89.7248 | 79.33 | 4.2 | 40 | 0.2499 | 94.7792 | 6659.4726
1000 | 3.3514 | 0 | 0 | 94.1718 | 88.9248 | 101498.9986 | 20 | 22.3669 | 26.4041 | 27.5384 | 89.7268 | 79.355 | 4.2 | 40 | 0.2484 | 94.3983 | 6625.8216
1002 | 3.3129 | 0 | 0 | 97.1559 | 90.6528 | 101494.4799 | 20 | 22.4041 | 26.4252 | 27.5545 | 89.7158 | 79.358 | 4.2 | 40 | 0.24554 | 92.9421 | 6527.5249
1004 | 3.3386 | 0 | 0 | 94.4868 | 93.2187 | 101506.2797 | 20 | 22.4332 | 26.4453 | 27.5716 | 89.6505 | 79.34 | 4.2 | 40 | 0.24744 | 93.4515 | 6568.7435
1006 | 3.3801 | 0 | 0 | 94.4815 | 89.5774 | 101504.7742 | 20 | 22.4031 | 26.4403 | 27.5906 | 89.5953 | 79.401 | 4.2 | 40 | 0.25052 | 95.2046 | 6681.2661
1008 | 3.3139 | 0 | 0 | 100.3752 | 95.0939 | 101500.5064 | 20 | 22.3729 | 26.4182 | 27.5635 | 89.5883 | 79.362 | 4.2 | 40 | 0.24561 | 93.5272 | 6564.5727
1010 | 3.3278 | 0 | 0 | 93.9267 | 88.2979 | 101504.0214 | 20 | 22.386 | 26.4001 | 27.5505 | 89.528 | 79.328 | 4.2 | 40 | 0.24664 | 93.1944 | 6546.6184
1012 | 3.3544 | 0 | 0 | 93.1587 | 89.8309 | 101504.5233 | 20 | 22.4081 | 26.4533 | 27.5746 | 89.4628 | 79.428 | 4.2 | 40 | 0.24861 | 94.6696 | 6641.1578
1014 | 3.3534 | 0 | 0 | 99.2558 | 97.1847 | 101498.9986 | 20 | 22.397 | 26.4343 | 27.5746 | 89.4196 | 79.462 | 4.2 | 40 | 0.24854 | 94.4538 | 6620.7873
1016 | 3.3539 | 0 | 0 | 93.4585 | 89.4765 | 101495.2327 | 20 | 22.3779 | 26.4262 | 27.5796 | 89.4086 | 79.413 | 4.2 | 40 | 0.24858 | 94.7263 | 6643.3767
1018 | 3.2754 | 0 | 0 | 97.1445 | 89.009 | 101501.0082 | 20 | 22.3749 | 26.386 | 27.5475 | 89.5331 | 79.477 | 4.2 | 40 | 0.24276 | 91.66 | 6420.7821
1020 | 3.3544 | 0 | 0 | 96.3476 | 95.1402 | 101506.2797 | 20 | 22.4 | 26.4172 | 27.5615 | 89.4286 | 79.517 | 4.2 | 40 | 0.24861 | 94.0114 | 6583.7858
1022 | 3.4092 | 0 | 0 | 94.033 | 90.6027 | 101502.0119 | 20 | 22.4061 | 26.4282 | 27.5565 | 89.4547 | 79.519 | 4.2 | 40 | 0.25268 | 95.6667 | 6700.1806
1024 | 3.3307 | 0 | 0 | 100.7994 | 93.4433 | 101495.9877 | 20 | 22.3779 | 26.3981 | 27.5485 | 89.3132 | 79.473 | 4.2 | 40 | 0.24686 | 93.4175 | 6544.6979
1026 | 3.3534 | 0 | 0 | 94.3692 | 87.8031 | 101506.7838 | 20 | 22.3508 | 26.38 | 27.5354 | 89.2509 | 79.385 | 4.2 | 40 | 0.24854 | 94.266 | 6611.1921
1028 | 3.3169 | 0 | 0 | 94.2561 | 89.1608 | 101509.042 | 20 | 22.388 | 26.4011 | 27.5364 | 89.3333 | 79.385 | 4.2 | 40 | 0.24583 | 92.867 | 6517.3263
1030 | 3.3944 | 0 | 0 | 101.4915 | 97.1179 | 101495.7368 | 20 | 22.399 | 26.3961 | 27.5274 | 89.3112 | 79.344 | 4.2 | 40 | 0.25158 | 94.6565 | 6648.9825
1032 | 3.3643 | 0 | 0 | 94.9254 | 89.9037 | 101496.9913 | 20 | 22.4211 | 26.4574 | 27.5916 | 89.2489 | 79.273 | 4.2 | 40 | 0.24935 | 94.736 | 6665.4607
1034 | 3.3268 | 0 | 0 | 96.9009 | 90.1565 | 101505.5269 | 20 | 22.4041 | 26.4584 | 27.5816 | 89.2419 | 79.357 | 4.2 | 40 | 0.24657 | 94.0991 | 6608.9059
1036 | 3.3352 | 0 | 0 | 97.7858 | 96.4865 | 101500.0046 | 20 | 22.396 | 26.4212 | 27.5766 | 89.3323 | 79.361 | 4.2 | 40 | 0.24719 | 93.6588 | 6576.5915
1038 | 3.3282 | 0 | 0 | 94.0572 | 90.0145 | 101495.4836 | 20 | 22.391 | 26.4101 | 27.5414 | 89.529 | 79.348 | 4.2 | 40 | 0.24668 | 93.3248 | 6554.0516
1040 | 3.3406 | 0 | 0 | 98.1812 | 89.6396 | 101500.5064 | 20 | 22.4533 | 26.4594 | 27.6067 | 89.6987 | 79.321 | 4.2 | 40 | 0.24759 | 93.3663 | 6567.2624
1042 | 3.3016 | 0 | 0 | 93.2991 | 91.3927 | 101501.2591 | 20 | 22.4392 | 26.4403 | 27.5746 | 89.529 | 79.241 | 4.2 | 40 | 0.2447 | 92.1606 | 6489.9803
1044 | 3.3554 | 0 | 0 | 93.3439 | 89.925 | 101499.5027 | 20 | 22.4252 | 26.4403 | 27.5746 | 89.5622 | 79.253 | 4.2 | 40 | 0.24869 | 93.992 | 6615.9114
1046 | 3.3806 | 0 | 0 | 100.319 | 95.0233 | 101499.2518 | 20 | 22.381 | 26.4081 | 27.5665 | 89.512 | 79.294 | 4.2 | 40 | 0.25055 | 94.9818 | 6675.5729
1048 | 3.3233 | 0 | 0 | 95.6646 | 88.4095 | 101504.7742 | 20 | 22.4031 | 26.4162 | 27.5585 | 89.4186 | 79.27 | 4.2 | 40 | 0.24631 | 93.0466 | 6544.8671
1050 | 3.3668 | 0 | 0 | 94.9771 | 88.6553 | 101502.7669 | 20 | 22.4473 | 26.4302 | 27.5856 | 89.2891 | 79.221 | 4.2 | 40 | 0.24953 | 93.555 | 6591.4312
1052 | 3.3658 | 0 | 0 | 99.1852 | 98.1629 | 101498.9986 | 20 | 22.4201 | 26.4302 | 27.5746 | 89.3292 | 79.263 | 4.2 | 40 | 0.24946 | 94.1645 | 6626.3045
1054 | 3.3796 | 0 | 0 | 94.379 | 88.8686 | 101498.7477 | 20 | 22.381 | 26.382 | 27.5475 | 89.4568 | 79.287 | 4.2 | 40 | 0.25048 | 94.3383 | 6631.1627
1056 | 3.3416 | 0 | 0 | 94.3054 | 91.2986 | 101501.7609 | 20 | 22.4011 | 26.4061 | 27.5454 | 89.1495 | 79.268 | 4.2 | 40 | 0.24766 | 93.3707 | 6567.662
1058 | 3.3144 | 0 | 0 | 98.6752 | 95.3671 | 101503.0178 | 20 | 22.395 | 26.4302 | 27.5716 | 89.0341 | 79.209 | 4.2 | 40 | 0.24565 | 93.3088 | 6569.4225
1060 | 3.3668 | 0 | 0 | 96.2649 | 89.3877 | 101500.0046 | 20 | 22.4141 | 26.4162 | 27.5665 | 89.0632 | 79.27 | 4.2 | 40 | 0.24953 | 94.0035 | 6613.454
1062 | 3.3327 | 0 | 0 | 96.5389 | 90.1762 | 101500.7573 | 20 | 22.381 | 26.379 | 27.5344 | 89.3724 | 79.404 | 4.2 | 40 | 0.24701 | 92.9591 | 6520.8088
1064 | 3.3396 | 0 | 0 | 95.4225 | 93.1117 | 101504.7742 | 20 | 22.3729 | 26.382 | 27.5183 | 89.4136 | 79.417 | 4.2 | 40 | 0.24752 | 93.4093 | 6549.9712
1066 | 3.3327 | 0 | 0 | 94.8329 | 90.6816 | 101497.995 | 20 | 22.4201 | 26.4182 | 27.5515 | 89.7268 | 79.473 | 4.2 | 40 | 0.24701 | 92.9589 | 6517.3878
1068 | 3.3544 | 0 | 0 | 101.871 | 96.0228 | 101497.7441 | 20 | 22.395 | 26.4312 | 27.5515 | 89.769 | 79.567 | 4.2 | 40 | 0.24861 | 94.4581 | 6608.6976
1070 | 3.308 | 0 | 0 | 94.1483 | 89.6852 | 101494.4799 | 20 | 22.3538 | 26.4091 | 27.5595 | 89.9357 | 79.526 | 4.2 | 40 | 0.24518 | 93.5919 | 6548.073
1072 | 3.3554 | 0 | 0 | 94.7919 | 90.1208 | 101502.7669 | 20 | 22.386 | 26.385 | 27.5485 | 90.024 | 79.599 | 4.2 | 40 | 0.24869 | 93.616 | 6545.0816
1074 | 3.3539 | 0 | 0 | 98.7936 | 97.9406 | 101498.7477 | 20 | 22.4 | 26.3931 | 27.5575 | 89.9076 | 79.593 | 4.2 | 40 | 0.24858 | 93.4336 | 6534.6244
1076 | 3.3559 | 0 | 0 | 94.637 | 89.8392 | 101495.4836 | 20 | 22.4232 | 26.4031 | 27.5706 | 89.6796 | 79.613 | 4.2 | 40 | 0.24872 | 93.1827 | 6517.43
1078 | 3.3352 | 0 | 0 | 98.3269 | 91.241 | 101499.2518 | 20 | 22.4282 | 26.4473 | 27.5846 | 89.4176 | 79.566 | 4.2 | 40 | 0.24719 | 93.5185 | 6546.8691
1080 | 3.3539 | 0 | 0 | 96.3901 | 93.1337 | 101504.7742 | 20 | 22.4051 | 26.4393 | 27.6067 | 89.3132 | 79.532 | 4.2 | 40 | 0.24858 | 94.3972 | 6609.645
1082 | 3.3658 | 0 | 0 | 93.1337 | 88.2835 | 101499.7536 | 20 | 22.396 | 26.4292 | 27.5876 | 89.2208 | 79.43 | 4.2 | 40 | 0.24946 | 94.7071 | 6642.1535
1084 | 3.3278 | 0 | 0 | 98.8619 | 94.4238 | 101498.4968 | 20 | 22.4181 | 26.4443 | 27.5886 | 89.1355 | 79.358 | 4.2 | 40 | 0.24664 | 93.4741 | 6566.5125
1086 | 3.3687 | 0 | 0 | 94.3563 | 89.9903 | 101502.2628 | 20 | 22.4513 | 26.4734 | 27.5967 | 89.0491 | 79.341 | 4.2 | 40 | 0.24968 | 94.5306 | 6646.5824
1088 | 3.3139 | 0 | 0 | 95.1675 | 89.2852 | 101502.5137 | 20 | 22.4181 | 26.4704 | 27.6208 | 88.9919 | 79.285 | 4.2 | 40 | 0.24561 | 93.6896 | 6590.0993
1090 | 3.3524 | 0 | 0 | 99.4607 | 97.3547 | 101495.9877 | 20 | 22.4121 | 26.4222 | 27.5756 | 89.011 | 79.283 | 4.2 | 40 | 0.24847 | 93.7916 | 6596.8071
1092 | 3.3584 | 0 | 0 | 94.9558 | 89.7808 | 101496.9913 | 20 | 22.4011 | 26.4122 | 27.5565 | 89.1716 | 79.322 | 4.2 | 40 | 0.24891 | 93.981 | 6604.3149
1094 | 3.3144 | 0 | 0 | 94.0922 | 90.8532 | 101499.7536 | 20 | 22.4402 | 26.4574 | 27.5997 | 89.256 | 79.346 | 4.2 | 40 | 0.24565 | 92.8905 | 6529.4251
1096 | 3.3549 | 0 | 0 | 97.3502 | 93.9874 | 101500.5064 | 20 | 22.4121 | 26.4463 | 27.5695 | 89.26 | 79.41 | 4.2 | 40 | 0.24865 | 94.4249 | 6626.5565
1098 | 3.3539 | 0 | 0 | 95.1053 | 89.6708 | 101504.2724 | 20 | 22.385 | 26.4041 | 27.5806 | 89.3132 | 79.47 | 4.2 | 40 | 0.24858 | 94.0447 | 6589.8016
1100 | 3.3041 | 0 | 0 | 100.4085 | 91.6819 | 101495.2327 | 20 | 22.393 | 26.4302 | 27.5645 | 89.3403 | 79.523 | 4.2 | 40 | 0.24488 | 93.0633 | 6515.8986
1102 | 3.2749 | 0 | 0 | 92.7246 | 91.332 | 101501.51 | 20 | 22.4372 | 26.4232 | 27.5736 | 89.4578 | 79.459 | 4.2 | 40 | 0.24272 | 91.0722 | 6388.5922
1104 | 3.3134 | 0 | 0 | 94.6757 | 90.8714 | 101504.5233 | 20 | 22.4081 | 26.4614 | 27.6157 | 89.3222 | 79.379 | 4.2 | 40 | 0.24558 | 93.6988 | 6578.7125
1106 | 3.346 | 0 | 0 | 99.9896 | 96.3006 | 101504.0214 | 20 | 22.397 | 26.4594 | 27.5806 | 89.2319 | 79.398 | 4.2 | 40 | 0.24799 | 94.8313 | 6654.7179
1108 | 3.3411 | 0 | 0 | 94.0975 | 88.6113 | 101492.2217 | 20 | 22.397 | 26.4152 | 27.6017 | 89.2268 | 79.54 | 4.2 | 40 | 0.24763 | 93.6612 | 6556.2742
1110 | 3.3421 | 0 | 0 | 95.1273 | 88.5157 | 101498.9986 | 20 | 22.4432 | 26.4523 | 27.6137 | 89.2529 | 79.498 | 4.2 | 40 | 0.2477 | 93.4779 | 6553.56
1112 | 3.3095 | 0 | 0 | 96.7468 | 95.4407 | 101499.7536 | 20 | 22.4432 | 26.4543 | 27.5706 | 89.1927 | 79.569 | 4.2 | 40 | 0.24529 | 92.6131 | 6484.8544
1114 | 3.3322 | 0 | 0 | 93.6482 | 90.4335 | 101495.9877 | 20 | 22.4071 | 26.4564 | 27.5947 | 89.2268 | 79.328 | 4.2 | 40 | 0.24697 | 94.136 | 6615.2109
1116 | 3.3139 | 0 | 0 | 98.3944 | 91.2091 | 101496.7404 | 20 | 22.38 | 26.4031 | 27.5655 | 89.1525 | 79.184 | 4.2 | 40 | 0.24561 | 93.0163 | 6549.9786
1118 | 3.3134 | 0 | 0 | 94.275 | 90.1967 | 101501.51 | 20 | 22.4181 | 26.4031 | 27.5756 | 89.1997 | 79.028 | 4.2 | 40 | 0.24558 | 92.1199 | 6509.1065
1120 | 3.3539 | 0 | 0 | 94.6742 | 88.8238 | 101503.0178 | 20 | 22.4211 | 26.4413 | 27.5605 | 89.4688 | 79.194 | 4.2 | 40 | 0.24858 | 94.0681 | 6627.6797
1122 | 3.3386 | 0 | 0 | 100.4154 | 95.377 | 101495.7368 | 20 | 22.4151 | 26.4383 | 27.5625 | 89.6596 | 79.283 | 4.2 | 40 | 0.24744 | 93.709 | 6591.3458
1124 | 3.3811 | 0 | 0 | 94.3039 | 88.9088 | 101503.5196 | 20 | 22.3779 | 26.3981 | 27.5374 | 89.5531 | 79.174 | 4.2 | 40 | 0.25059 | 94.8298 | 6678.6165
1126 | 3.2749 | 0 | 0 | 97.1301 | 89.1517 | 101505.276 | 20 | 22.4332 | 26.4222 | 27.5214 | 89.2971 | 79.136 | 4.2 | 40 | 0.24272 | 91.1411 | 6429.3891
1128 | 3.2892 | 0 | 0 | 100.4032 | 96.0539 | 101496.9913 | 20 | 22.4372 | 26.4493 | 27.5786 | 89.3945 | 79.09 | 4.2 | 40 | 0.24379 | 92.0697 | 6500.6307
1130 | 3.2878 | 0 | 0 | 93.6694 | 89.1797 | 101495.9877 | 20 | 22.4382 | 26.4513 | 27.5826 | 89.5602 | 79.203 | 4.2 | 40 | 0.24368 | 92.0512 | 6486.5016
1132 | 3.3011 | 0 | 0 | 95.7648 | 91.9225 | 101503.0178 | 20 | 22.4131 | 26.4393 | 27.5545 | 89.8684 | 79.193 | 4.2 | 40 | 0.24466 | 92.7253 | 6532.2627
1134 | 3.3011 | 0 | 0 | 98.6456 | 94.6052 | 101501.7609 | 20 | 22.4242 | 26.4473 | 27.5575 | 89.7479 | 79.12 | 4.2 | 40 | 0.24466 | 92.6559 | 6537.0471
1136 | 3.3016 | 0 | 0 | 94.4769 | 89.4765 | 101497.2422 | 20 | 22.4543 | 26.4443 | 27.5736 | 89.6566 | 79.13 | 4.2 | 40 | 0.2447 | 91.906 | 6486.4506
1138 | 3.3544 | 0 | 0 | 98.6388 | 92.3292 | 101494.9818 | 20 | 22.4272 | 26.4232 | 27.5706 | 89.6425 | 79.032 | 4.2 | 40 | 0.24861 | 93.5177 | 6608.4611
1140 | 3.3154 | 0 | 0 | 95.8748 | 91.2091 | 101500.7573 | 20 | 22.4272 | 26.4373 | 27.5645 | 89.525 | 78.989 | 4.2 | 40 | 0.24572 | 92.7556 | 6559.5902
1142 | 3.3914 | 0 | 0 | 94.5596 | 89.4059 | 101504.5233 | 20 | 22.4171 | 26.4373 | 27.5826 | 89.2319 | 78.966 | 4.2 | 40 | 0.25136 | 95.1204 | 6728.3665
1144 | 3.3307 | 0 | 0 | 100.5785 | 97.8746 | 101499.2518 | 20 | 22.4071 | 26.4122 | 27.5685 | 89.0431 | 79.091 | 4.2 | 40 | 0.24686 | 93.0672 | 6567.4528
1146 | 3.3139 | 0 | 0 | 94.9148 | 89.4378 | 101495.9877 | 20 | 22.4473 | 26.4222 | 27.5675 | 88.8744 | 79.114 | 4.2 | 40 | 0.24561 | 91.9014 | 6487.1467
1148 | 3.2493 | 0 | 0 | 96.5784 | 90.205 | 101498.7477 | 20 | 22.4603 | 26.4403 | 27.5836 | 89.0521 | 79.195 | 4.2 | 40 | 0.24082 | 90.2216 | 6360.9515
1150 | 3.349 | 0 | 0 | 98.9416 | 96.5404 | 101496.4895 | 20 | 22.4161 | 26.4383 | 27.5926 | 89.2228 | 79.153 | 4.2 | 40 | 0.24821 | 93.9765 | 6625.4279
1152 | 3.3396 | 0 | 0 | 94.1476 | 90.482 | 101498.2459 | 20 | 22.392 | 26.4142 | 27.5575 | 89.0421 | 79.075 | 4.2 | 40 | 0.24752 | 93.7134 | 6613.1586
1154 | 3.3144 | 0 | 0 | 95.273 | 91.8018 | 101502.5137 | 20 | 22.4442 | 26.4332 | 27.5685 | 88.8865 | 78.99 | 4.2 | 40 | 0.24565 | 92.2402 | 6524.9932
1156 | 3.3144 | 0 | 0 | 96.825 | 91.4375 | 101492.7235 | 20 | 22.4302 | 26.4302 | 27.6007 | 89.023 | 79.007 | 4.2 | 40 | 0.24565 | 92.4957 | 6539.4776
1158 | 3.3677 | 0 | 0 | 94.7061 | 88.6827 | 101498.2459 | 20 | 22.4051 | 26.4252 | 27.5685 | 89.0491 | 79.021 | 4.2 | 40 | 0.2496 | 94.4559 | 6673.447
1160 | 3.2878 | 0 | 0 | 100.5262 | 95.4703 | 101489.4594 | 20 | 22.4051 | 26.4091 | 27.5575 | 88.8935 | 78.997 | 4.2 | 40 | 0.24368 | 91.844 | 6491.6683
1162 | 3.3134 | 0 | 0 | 93.6763 | 92.2958 | 101500.7573 | 20 | 22.4161 | 26.3951 | 27.5575 | 88.7178 | 78.924 | 4.2 | 40 | 0.24558 | 91.9806 | 6510.9941
1164 | 3.3401 | 0 | 0 | 93.7962 | 90.6361 | 101497.2422 | 20 | 22.4272 | 26.4332 | 27.5625 | 88.7399 | 78.987 | 4.2 | 40 | 0.24755 | 93.3527 | 6602.0479
1166 | 3.3278 | 0 | 0 | 100.7956 | 94.8033 | 101491.4667 | 20 | 22.4412 | 26.4142 | 27.5786 | 88.5983 | 79.012 | 4.2 | 40 | 0.24664 | 92.2381 | 6521.9617
1168 | 3.3549 | 0 | 0 | 93.6338 | 88.4853 | 101496.2386 | 20 | 22.392 | 26.3901 | 27.5525 | 88.4518 | 79.012 | 4.2 | 40 | 0.24865 | 93.5787 | 6611.0019
1170 | 3.3559 | 0 | 0 | 94.5657 | 89.7019 | 101497.7441 | 20 | 22.4191 | 26.3931 | 27.5304 | 88.505 | 79.055 | 4.2 | 40 | 0.24872 | 93.0416 | 6571.2162
1172 | 3.3549 | 0 | 0 | 97.6568 | 97.3342 | 101492.7235 | 20 | 22.4352 | 26.4232 | 27.5485 | 88.4688 | 79.031 | 4.2 | 40 | 0.24865 | 93.3434 | 6597.1988
1174 | 3.3791 | 0 | 0 | 95.8885 | 89.9227 | 101496.9913 | 20 | 22.4422 | 26.4523 | 27.5816 | 88.4789 | 78.92 | 4.2 | 40 | 0.25044 | 94.5373 | 6695.54
1176 | 3.3421 | 0 | 0 | 99.0205 | 90.8865 | 101490.2121 | 20 | 22.4061 | 26.4302 | 27.5595 | 88.2801 | 78.951 | 4.2 | 40 | 0.2477 | 93.8294 | 6637.5116
1178 | 3.3149 | 0 | 0 | 95.314 | 92.9014 | 101497.7441 | 20 | 22.4221 | 26.4242 | 27.5766 | 88.3453 | 79.002 | 4.2 | 40 | 0.24569 | 92.556 | 6543.3924
1180 | 3.3608 | 0 | 0 | 94.7478 | 90.2081 | 101492.9745 | 20 | 22.388 | 26.37 | 27.5535 | 88.4688 | 79.029 | 4.2 | 40 | 0.24909 | 93.3671 | 6593.6042
1182 | 3.3154 | 0 | 0 | 100.6537 | 94.7517 | 101492.4726 | 20 | 22.4272 | 26.4172 | 27.5645 | 88.4166 | 79.064 | 4.2 | 40 | 0.24572 | 92.291 | 6518.088
1184 | 3.3381 | 0 | 0 | 93.202 | 90.693 | 101496.4895 | 20 | 22.4754 | 26.4513 | 27.5896 | 88.5009 | 79.047 | 4.2 | 40 | 0.24741 | 92.5955 | 6547.1356
1186 | 3.2843 | 0 | 0 | 94.3456 | 89.0925 | 101501.0082 | 20 | 22.4312 | 26.4624 | 27.6107 | 88.7168 | 79.047 | 4.2 | 40 | 0.24342 | 92.3688 | 6526.0055
1188 | 3.3278 | 0 | 0 | 100.6203 | 96.3947 | 101491.9708 | 20 | 22.4282 | 26.4282 | 27.5766 | 88.6224 | 79.129 | 4.2 | 40 | 0.24664 | 92.8678 | 6551.422
1190 | 3.3885 | 0 | 0 | 94.225 | 87.451 | 101489.7103 | 20 | 22.4473 | 26.4363 | 27.5665 | 88.5993 | 79.132 | 4.2 | 40 | 0.25114 | 94.3011 | 6654.424
1192 | 3.2843 | 0 | 0 | 94.3267 | 90.8152 | 101501.51 | 20 | 22.4724 | 26.4684 | 27.5906 | 88.6515 | 78.995 | 4.2 | 40 | 0.24342 | 91.5631 | 6479.7477
1194 | 3.3011 | 0 | 0 | 98.4103 | 96.0099 | 101499.5027 | 20 | 22.4392 | 26.4634 | 27.6067 | 88.6706 | 79.044 | 4.2 | 40 | 0.24466 | 92.6789 | 6549.194
1196 | 3.3411 | 0 | 0 | 96.3992 | 89.8028 | 101490.463 | 20 | 22.4031 | 26.4172 | 27.5716 | 88.7379 | 79.051 | 4.2 | 40 | 0.24763 | 93.5676 | 6606.9526
1198 | 3.3194 | 0 | 0 | 97.6788 | 91.3358 | 101491.7176 | 20 | 22.4503 | 26.4393 | 27.5906 | 88.6445 | 78.956 | 4.2 | 40 | 0.24602 | 92.3776 | 6539.3425
1200 | 3.3682 | 0 | 0 | 95.7519 | 92.5319 | 101496.9913 | 20 | 22.4312 | 26.4443 | 27.5987 | 88.3614 | 78.9 | 4.2 | 40 | 0.24964 | 94.3043 | 6680.0983
1202 | 3.385 | 0 | 0 | 94.6955 | 91.1271 | 101491.7176 | 20 | 22.4392 | 26.4473 | 27.5665 | 88.256 | 78.917 | 4.2 | 40 | 0.25088 | 94.6556 | 6703.9218
1204 | 3.3278 | 0 | 0 | 101.3299 | 95.9249 | 101493.9781 | 20 | 22.4111 | 26.4393 | 27.5665 | 88.1596 | 78.771 | 4.2 | 40 | 0.24664 | 93.5208 | 6637.397
1206 | 3.3668 | 0 | 0 | 94.3783 | 89.7497 | 101495.7368 | 20 | 22.4 | 26.383 | 27.5284 | 87.9126 | 78.795 | 4.2 | 40 | 0.24953 | 93.5553 | 6635.7191
1208 | 3.3273 | 0 | 0 | 94.1422 | 89.5562 | 101498.9986 | 20 | 22.4422 | 26.4332 | 27.5635 | 87.9297 | 78.781 | 4.2 | 40 | 0.2466 | 92.644 | 6577.6393
1210 | 3.3524 | 0 | 0 | 99.6777 | 97.7956 | 101493.7272 | 20 | 22.4221 | 26.4332 | 27.5746 | 87.9076 | 78.686 | 4.2 | 40 | 0.24847 | 93.815 | 6669.6486
1212 | 3.3391 | 0 | 0 | 93.4661 | 89.9242 | 101495.7368 | 20 | 22.4131 | 26.4242 | 27.5485 | 87.9899 | 78.684 | 4.2 | 40 | 0.24748 | 93.4421 | 6642.3062
1214 | 3.3663 | 0 | 0 | 94.7805 | 89.8491 | 101495.4836 | 20 | 22.4101 | 26.4112 | 27.5485 | 88.2138 | 78.679 | 4.2 | 40 | 0.24949 | 93.966 | 6679.7835
1216 | 3.3401 | 0 | 0 | 99.7574 | 95.9667 | 101491.4667 | 20 | 22.4463 | 26.4533 | 27.5605 | 88.1767 | 78.694 | 4.2 | 40 | 0.24755 | 93.376 | 6640.3371
1218 | 3.3332 | 0 | 0 | 95.8377 | 89.333 | 101488.9576 | 20 | 22.4272 | 26.4383 | 27.5665 | 88.2911 | 78.69 | 4.2 | 40 | 0.24704 | 93.2762 | 6631.4635
1220 | 3.3668 | 0 | 0 | 97.6886 | 90.1618 | 101490.2121 | 20 | 22.4191 | 26.4182 | 27.5585 | 88.3242 | 78.763 | 4.2 | 40 | 0.24953 | 93.9327 | 6668.5272
1222 | 3.3539 | 0 | 0 | 93.3325 | 93.7256 | 101498.7477 | 20 | 22.4081 | 26.4041 | 27.5444 | 88.4086 | 78.872 | 4.2 | 40 | 0.24858 | 93.5041 | 6623.9887
1224 | 3.3401 | 0 | 0 | 95.1607 | 91.4914 | 101495.7368 | 20 | 22.4603 | 26.4764 | 27.6037 | 88.5732 | 78.922 | 4.2 | 40 | 0.24755 | 93.5866 | 6630.0952
1226 | 3.3194 | 0 | 0 | 101.1052 | 94.587 | 101491.9708 | 20 | 22.4704 | 26.4805 | 27.6077 | 88.9467 | 78.946 | 4.2 | 40 | 0.24602 | 92.8659 | 6577.4164
1228 | 3.3544 | 0 | 0 | 92.1812 | 88.4041 | 101496.2386 | 20 | 22.4453 | 26.4614 | 27.6208 | 88.9879 | 78.957 | 4.2 | 40 | 0.24861 | 93.9877 | 6652.6155
1230 | 3.3692 | 0 | 0 | 93.9495 | 89.4583 | 101496.9913 | 20 | 22.4593 | 26.4614 | 27.6067 | 88.9668 | 78.911 | 4.2 | 40 | 0.24971 | 94.0721 | 6665.6735
1232 | 3.2878 | 0 | 0 | 99.7058 | 97.25 | 101491.9708 | 20 | 22.4483 | 26.4473 | 27.6097 | 88.7871 | 78.937 | 4.2 | 40 | 0.24368 | 91.7286 | 6495.357
1234 | 3.3401 | 0 | 0 | 93.9851 | 89.0583 | 101487.9516 | 20 | 22.4613 | 26.4453 | 27.6127 | 88.8202 | 78.981 | 4.2 | 40 | 0.24755 | 92.8376 | 6570.2857
1236 | 3.3781 | 0 | 0 | 96.6967 | 89.3611 | 101495.4836 | 20 | 22.4483 | 26.4774 | 27.6147 | 89.0361 | 79.032 | 4.2 | 40 | 0.25037 | 94.9594 | 6712.8393
1238 | 3.3273 | 0 | 0 | 97.9375 | 94.354 | 101491.9708 | 20 | 22.4312 | 26.4473 | 27.6047 | 88.7248 | 79.04 | 4.2 | 40 | 0.2466 | 93.2269 | 6587.4512
1240 | 3.35 | 0 | 0 | 93.9874 | 90.3492 | 101488.9576 | 20 | 22.4071 | 26.4132 | 27.5936 | 88.7289 | 79.018 | 4.2 | 40 | 0.24829 | 93.6287 | 6615.5922
1242 | 3.3396 | 0 | 0 | 98.594 | 93.8759 | 101487.1989 | 20 | 22.4724 | 26.4905 | 27.5856 | 88.9477 | 79.006 | 4.2 | 40 | 0.24752 | 93.6194 | 6623.9818
1244 | 3.3668 | 0 | 0 | 96.1746 | 90.4972 | 101499.7536 | 20 | 22.4422 | 26.4473 | 27.6067 | 88.9377 | 78.889 | 4.2 | 40 | 0.24953 | 94.0741 | 6666.3947
1246 | 3.3406 | 0 | 0 | 96.3621 | 89.3376 | 101496.4895 | 20 | 22.4232 | 26.4423 | 27.5967 | 88.775 | 78.879 | 4.2 | 40 | 0.24759 | 93.6707 | 6636.7436
1248 | 3.3278 | 0 | 0 | 100.3357 | 97.0686 | 101492.4726 | 20 | 22.4151 | 26.4373 | 27.5776 | 88.8895 | 78.937 | 4.2 | 40 | 0.24664 | 93.3808 | 6608.4726
1250 | 3.3327 | 0 | 0 | 93.9275 | 87.3849 | 101491.9708 | 20 | 22.4262 | 26.4292 | 27.5535 | 88.9256 | 78.947 | 4.2 | 40 | 0.24701 | 93.0756 | 6586.9973
1252 | 3.4028 | 0 | 0 | 96.1663 | 90.227 | 101491.9708 | 20 | 22.4453 | 26.4905 | 27.5987 | 89.0321 | 79.089 | 4.2 | 40 | 0.2522 | 96.0349 | 6781.6759
1254 | 3.3712 | 0 | 0 | 99.1753 | 96.4167 | 101495.7368 | 20 | 22.4141 | 26.4443 | 27.5936 | 89.3132 | 79.126 | 4.2 | 40 | 0.24986 | 94.7889 | 6685.6483
1256 | 3.3016 | 0 | 0 | 95.037 | 90.3986 | 101494.229 | 20 | 22.4141 | 26.4252 | 27.5947 | 89.4166 | 79.177 | 4.2 | 40 | 0.2447 | 92.3921 | 6510.7375
1258 | 3.3307 | 0 | 0 | 100.6203 | 92.8885 | 101491.9708 | 20 | 22.4282 | 26.4383 | 27.5716 | 89.2228 | 79.187 | 4.2 | 40 | 0.24686 | 93.1838 | 6567.0031
1260 | 3.2907 | 0 | 0 | 94.5331 | 88.9301 | 101497.995 | 20 | 22.4402 | 26.4574 | 27.5856 | 88.9096 | 79.133 | 4.2 | 40 | 0.24389 | 92.2264 | 6507.101
1262 | 3.3564 | 0 | 0 | 94.3031 | 88.9528 | 101494.7308 | 20 | 22.4503 | 26.4855 | 27.5997 | 88.772 | 79.148 | 4.2 | 40 | 0.24876 | 94.4899 | 6666.2235
1264 | 3.3401 | 0 | 0 | 100.9808 | 97.6833 | 101490.714 | 20 | 22.4362 | 26.4423 | 27.5776 | 88.7268 | 79.175 | 4.2 | 40 | 0.24755 | 93.3526 | 6581.2215
1266 | 3.3273 | 0 | 0 | 95.9302 | 89.1539 | 101488.7067 | 20 | 22.4081 | 26.4322 | 27.5756 | 88.6977 | 79.13 | 4.2 | 40 | 0.2466 | 93.4136 | 6587.4765
1268 | 3.3129 | 0 | 0 | 97.1855 | 89.0287 | 101497.2422 | 20 | 22.4633 | 26.4634 | 27.5886 | 88.7489 | 79.066 | 4.2 | 40 | 0.24554 | 92.4543 | 6533.5632
1270 | 3.3559 | 0 | 0 | 98.4187 | 95.2852 | 101490.9649 | 20 | 22.4412 | 26.4714 | 27.6228 | 88.5933 | 78.96 | 4.2 | 40 | 0.24872 | 94.3584 | 6678.0243
1272 | 3.3366 | 0 | 0 | 95.758 | 90.2969 | 101488.9576 | 20 | 22.4302 | 26.4654 | 27.5957 | 88.5532 | 78.91 | 4.2 | 40 | 0.2473 | 93.934 | 6652.5735
1274 | 3.3278 | 0 | 0 | 98.166 | 92.6821 | 101486.4462 | 20 | 22.4332 | 26.4493 | 27.5916 | 88.5783 | 78.845 | 4.2 | 40 | 0.24664 | 93.2408 | 6611.4418
1276 | 3.3672 | 0 | 0 | 96.7392 | 93.1739 | 101493.4763 | 20 | 22.4573 | 26.4322 | 27.5786 | 88.9046 | 78.85 | 4.2 | 40 | 0.24957 | 93.3799 | 6623.5459
1278 | 3.3263 | 0 | 0 | 96.0312 | 88.8246 | 101491.7176 | 20 | 22.4905 | 26.4885 | 27.6368 | 88.9337 | 78.977 | 4.2 | 40 | 0.24653 | 92.7794 | 6570.0215
1280 | 3.3426 | 0 | 0 | 101.1971 | 97.1718 | 101488.7067 | 20 | 22.4704 | 26.4724 | 27.6127 | 89.004 | 79.277 | 4.2 | 40 | 0.24774 | 93.3277 | 6571.6084
1282 | 3.3574 | 0 | 0 | 93.416 | 90.5799 | 101489.2085 | 20 | 22.4463 | 26.4805 | 27.6047 | 89.1305 | 79.418 | 4.2 | 40 | 0.24883 | 94.4942 | 6634.4626
1284 | 3.3732 | 0 | 0 | 94.8738 | 91.5233 | 101497.7441 | 20 | 22.4463 | 26.5015 | 27.6047 | 89.2459 | 79.469 | 4.2 | 40 | 0.25 | 95.4353 | 6694.5399
1286 | 3.3668 | 0 | 0 | 100.2674 | 96.5343 | 101491.7176 | 20 | 22.4432 | 26.5126 | 27.6428 | 88.7078 | 79.603 | 4.2 | 40 | 0.24953 | 95.584 | 6688.9009
1288 | 3.3149 | 0 | 0 | 93.8668 | 88.011 | 101487.9516 | 20 | 22.4764 | 26.5076 | 27.6479 | 88.8523 | 79.657 | 4.2 | 40 | 0.24569 | 93.2294 | 6521.7521
1290 | 3.3011 | 0 | 0 | 95.4741 | 89.4218 | 101491.7176 | 20 | 22.4352 | 26.4855 | 27.6288 | 88.8594 | 79.845 | 4.2 | 40 | 0.24466 | 93.2804 | 6499.2649
1292 | 3.3668 | 0 | 0 | 96.6998 | 95.4218 | 101497.4932 | 20 | 22.4432 | 26.5096 | 27.6228 | 88.9809 | 79.999 | 4.2 | 40 | 0.24953 | 95.5132 | 6637.9606
1294 | 3.2616 | 0 | 0 | 94.9376 | 89.815 | 101488.9576 | 20 | 22.4081 | 26.4734 | 27.6228 | 89.5762 | 79.961 | 4.2 | 40 | 0.24174 | 92.5072 | 6429.3656
1296 | 3.3144 | 0 | 0 | 101.5074 | 93.6148 | 101491.4667 | 20 | 22.4734 | 26.5086 | 27.6358 | 90.0571 | 79.993 | 4.2 | 40 | 0.24565 | 93.3084 | 6488.8048
1298 | 3.2739 | 0 | 0 | 93.6292 | 88.5749 | 101487.4498 | 20 | 22.4633 | 26.5267 | 27.6579 | 90.0913 | 80.083 | 4.2 | 40 | 0.24265 | 92.8112 | 6443.0196
1300 | 3.3115 | 0 | 0 | 96.0001 | 89.563 | 101494.9818 | 20 | 22.4352 | 26.5226 | 27.6529 | 90.1736 | 80.155 | 4.2 | 40 | 0.24543 | 94.4319 | 6544.1621
1302 | 3.3139 | 0 | 0 | 99.2505 | 97.5862 | 101492.7235 | 20 | 22.4191 | 26.4885 | 27.6479 | 90.3644 | 80.128 | 4.2 | 40 | 0.24561 | 94.0844 | 6521.3099
1304 | 3.3282 | 0 | 0 | 94.927 | 89.1729 | 101486.6971 | 20 | 22.4643 | 26.5236 | 27.6218 | 90.4176 | 80.141 | 4.2 | 40 | 0.24668 | 94.2573 | 6536.9474
1306 | 3.3396 | 0 | 0 | 95.0552 | 89.3505 | 101489.2085 | 20 | 22.4694 | 26.5206 | 27.6479 | 90.2951 | 80.253 | 4.2 | 40 | 0.24752 | 94.3917 | 6534.1472
1308 | 3.3105 | 0 | 0 | 97.2189 | 95.8354 | 101498.9986 | 20 | 22.4453 | 26.5076 | 27.6459 | 89.9347 | 80.197 | 4.2 | 40 | 0.24536 | 93.8238 | 6498.4193
1310 | 3.3416 | 0 | 0 | 93.589 | 91.6735 | 101486.6971 | 20 | 22.4201 | 26.4805 | 27.6298 | 89.9256 | 80.131 | 4.2 | 40 | 0.24766 | 94.6585 | 6560.8792
1312 | 3.3011 | 0 | 0 | 100.6355 | 91.8071 | 101488.7067 | 20 | 22.4262 | 26.4965 | 27.6238 | 90.0039 | 80.104 | 4.2 | 40 | 0.24466 | 93.743 | 6501.1487
1314 | 3.3016 | 0 | 0 | 95.3171 | 92.8627 | 101493.2254 | 20 | 22.4503 | 26.5206 | 27.67 | 89.9889 | 79.983 | 4.2 | 40 | 0.2447 | 93.7569 | 6518.5089
1316 | 3.3134 | 0 | 0 | 93.0494 | 89.2351 | 101490.2121 | 20 | 22.4362 | 26.5076 | 27.68 | 89.7861 | 79.974 | 4.2 | 40 | 0.24558 | 94.1166 | 6542.9434
1318 | 3.3011 | 0 | 0 | 100.5436 | 97.0815 | 101490.2121 | 20 | 22.4252 | 26.5086 | 27.6368 | 89.763 | 80.05 | 4.2 | 40 | 0.24466 | 94.0438 | 6528.0019
1320 | 3.3554 | 0 | 0 | 95.075 | 88.7859 | 101491.9708 | 20 | 22.4171 | 26.4985 | 27.6318 | 89.3192 | 80.071 | 4.2 | 40 | 0.24869 | 95.5439 | 6628.7894
1322 | 3.312 | 0 | 0 | 94.6955 | 88.8428 | 101497.2422 | 20 | 22.4834 | 26.5498 | 27.677 | 89.3845 | 80.235 | 4.2 | 40 | 0.24547 | 93.9583 | 6507.7604
1324 | 3.3041 | 0 | 0 | 100.0405 | 98.2001 | 101487.7007 | 20 | 22.4463 | 26.5397 | 27.686 | 89.775 | 80.399 | 4.2 | 40 | 0.24488 | 94.3596 | 6512.8658
1326 | 3.3268 | 0 | 0 | 95.6494 | 90.4122 | 101488.4557 | 20 | 22.4412 | 26.5267 | 27.678 | 90.1586 | 80.396 | 4.2 | 40 | 0.24657 | 94.8216 | 6544.5278
1328 | 3.3139 | 0 | 0 | 95.6024 | 91.1355 | 101493.9781 | 20 | 22.4352 | 26.5156 | 27.6489 | 90.3915 | 80.301 | 4.2 | 40 | 0.24561 | 94.3397 | 6521.2771
1330 | 3.3672 | 0 | 0 | 97.9429 | 94.9884 | 101496.9913 | 20 | 22.4633 | 26.5508 | 27.6569 | 90.4658 | 80.289 | 4.2 | 40 | 0.24957 | 96.0226 | 6642.2112
1332 | 3.31 | 0 | 0 | 96.0494 | 89.4871 | 101488.7067 | 20 | 22.4322 | 26.5427 | 27.6619 | 90.3152 | 80.168 | 4.2 | 40 | 0.24532 | 94.9231 | 6576.3757
1334 | 3.3149 | 0 | 0 | 99.1738 | 93.1284 | 101491.2158 | 20 | 22.4543 | 26.5367 | 27.6509 | 90.1786 | 80.135 | 4.2 | 40 | 0.24569 | 94.4142 | 6547.3682
1336 | 3.3011 | 0 | 0 | 93.3993 | 91.9445 | 101496.4895 | 20 | 22.4221 | 26.5036 | 27.6449 | 90.3031 | 80.228 | 4.2 | 40 | 0.24466 | 93.9975 | 6504.3597
1338 | 3.3811 | 0 | 0 | 94.9809 | 89.7163 | 101497.7441 | 20 | 22.4684 | 26.5538 | 27.6679 | 90.3885 | 80.111 | 4.2 | 40 | 0.25059 | 96.3693 | 6687.3653
1340 | 3.3534 | 0 | 0 | 101.5704 | 96.0926 | 101488.7067 | 20 | 22.4814 | 26.5488 | 27.689 | 90.5089 | 80.112 | 4.2 | 40 | 0.24854 | 95.1583 | 6604.7101
1342 | 3.3337 | 0 | 0 | 93.8174 | 87.9549 | 101487.9516 | 20 | 22.4623 | 26.5216 | 27.684 | 90.5812 | 80.114 | 4.2 | 40 | 0.24708 | 94.4111 | 6550.4513
1344 | 3.3006 | 0 | 0 | 94.2485 | 90.3325 | 101495.4836 | 20 | 22.4402 | 26.5216 | 27.6569 | 90.6846 | 80.049 | 4.2 | 40 | 0.24463 | 93.9833 | 6525.6248
1346 | 3.3539 | 0 | 0 | 100.0595 | 98.9173 | 101491.4667 | 20 | 22.4372 | 26.5347 | 27.6569 | 90.6485 | 80.032 | 4.2 | 40 | 0.24858 | 95.8777 | 6658.7745
1348 | 3.3702 | 0 | 0 | 96.1587 | 89.4006 | 101490.463 | 20 | 22.4322 | 26.5407 | 27.6298 | 90.6867 | 80.105 | 4.2 | 40 | 0.24979 | 96.6032 | 6700.0834
1350 | 3.3406 | 0 | 0 | 96.6155 | 91.0232 | 101483.182 | 20 | 22.4674 | 26.5377 | 27.6679 | 90.5642 | 79.99 | 4.2 | 40 | 0.24759 | 94.8644 | 6596.6637
1352 | 3.3421 | 0 | 0 | 96.8015 | 89.3179 | 101490.2121 | 20 | 22.4563 | 26.5377 | 27.681 | 90.4367 | 80.015 | 4.2 | 40 | 0.2477 | 95.1641 | 6613.3574
1354 | 3.2971 | 0 | 0 | 95.1562 | 89.475 | 101491.9708 | 20 | 22.4453 | 26.5267 | 27.681 | 90.3624 | 79.961 | 4.2 | 40 | 0.24437 | 93.8849 | 6529.3362
1356 | 3.3357 | 0 | 0 | 100.1763 | 98.0248 | 101485.6934 | 20 | 22.4342 | 26.5086 | 27.6539 | 90.4256 | 79.803 | 4.2 | 40 | 0.24722 | 94.8178 | 6611.1058
1358 | 3.3149 | 0 | 0 | 95.4491 | 89.6715 | 101486.1953 | 20 | 22.4453 | 26.5327 | 27.6679 | 90.4778 | 79.795 | 4.2 | 40 | 0.24569 | 94.5304 | 6593.256
1360 | 3.3273 | 0 | 0 | 94.5976 | 89.5175 | 101489.7103 | 20 | 22.4593 | 26.5246 | 27.6569 | 90.2047 | 79.707 | 4.2 | 40 | 0.2466 | 94.3693 | 6593.7527
1362 | 3.3406 | 0 | 0 | 97.338 | 97.0914 | 101492.7235 | 20 | 22.4262 | 26.4975 | 27.6298 | 90.027 | 79.498 | 4.2 | 40 | 0.24759 | 94.888 | 6650.4249
1364 | 3.3268 | 0 | 0 | 94.0641 | 90.5549 | 101487.7007 | 20 | 22.4051 | 26.4714 | 27.6177 | 89.8122 | 79.498 | 4.2 | 40 | 0.24657 | 94.3789 | 6612.2992
1366 | 3.3021 | 0 | 0 | 99.1564 | 90.2392 | 101489.4594 | 20 | 22.4312 | 26.4945 | 27.6268 | 89.3895 | 79.504 | 4.2 | 40 | 0.24474 | 93.6091 | 6560.6789
1368 | 3.3668 | 0 | 0 | 95.8331 | 93.2399 | 101490.714 | 20 | 22.4513 | 26.5126 | 27.6489 | 89.4005 | 79.428 | 4.2 | 40 | 0.24953 | 95.3952 | 6697.1362
1370 | 3.3001 | 0 | 0 | 93.8402 | 88.9908 | 101495.4836 | 20 | 22.4342 | 26.5126 | 27.6559 | 89.3855 | 79.445 | 4.2 | 40 | 0.24459 | 93.9 | 6588.2228
1372 | 3.3781 | 0 | 0 | 100.5436 | 97.0071 | 101483.6839 | 20 | 22.4392 | 26.4795 | 27.6368 | 89.6495 | 79.448 | 4.2 | 40 | 0.25037 | 95.2198 | 6681.0633
1374 | 3.3416 | 0 | 0 | 92.0006 | 90.0206 | 101491.2158 | 20 | 22.4684 | 26.5015 | 27.6519 | 89.7068 | 79.295 | 4.2 | 40 | 0.24766 | 94.0261 | 6618.4487
1376 | 3.3134 | 0 | 0 | 94.3175 | 89.7937 | 101494.4799 | 20 | 22.4814 | 26.5287 | 27.6679 | 89.774 | 79.336 | 4.2 | 40 | 0.24558 | 93.5592 | 6582.3489
1378 | 3.3282 | 0 | 0 | 100.6597 | 96.8151 | 101490.2121 | 20 | 22.4653 | 26.5397 | 27.6579 | 89.9537 | 79.449 | 4.2 | 40 | 0.24668 | 94.6072 | 6641.0027
1380 | 3.2878 | 0 | 0 | 94.9452 | 86.5904 | 101490.463 | 20 | 22.4432 | 26.4875 | 27.669 | 90.0411 | 79.476 | 4.2 | 40 | 0.24368 | 92.7654 | 6506.1123
1382 | 3.2868 | 0 | 0 | 95.7542 | 90.1064 | 101495.4836 | 20 | 22.4854 | 26.5126 | 27.6509 | 89.9638 | 79.472 | 4.2 | 40 | 0.2436 | 92.3458 | 6481.9337
1384 | 3.3672 | 0 | 0 | 98.4149 | 96.1959 | 101491.7176 | 20 | 22.4613 | 26.5236 | 27.679 | 90.1565 | 79.686 | 4.2 | 40 | 0.24957 | 95.4327 | 6670.7372
1386 | 3.3445 | 0 | 0 | 95.0325 | 89.56 | 101488.2026 | 20 | 22.4734 | 26.5407 | 27.679 | 90.3583 | 79.752 | 4.2 | 40 | 0.24788 | 94.9062 | 6627.6908
1388 | 3.3342 | 0 | 0 | 96.5609 | 91.3548 | 101483.6839 | 20 | 22.4382 | 26.5066 | 27.6579 | 90.6897 | 79.83 | 4.2 | 40 | 0.24711 | 94.6355 | 6595.7563
1390 | 3.2996 | 0 | 0 | 96.9016 | 90.8228 | 101487.7007 | 20 | 22.4402 | 26.4795 | 27.6338 | 90.8051 | 79.927 | 4.2 | 40 | 0.24455 | 92.9841 | 6469.946
1392 | 3.3391 | 0 | 0 | 93.3477 | 89.8271 | 101493.2254 | 20 | 22.4874 | 26.5437 | 27.6549 | 91.0903 | 79.93 | 4.2 | 40 | 0.24748 | 94.4947 | 6580.119
1394 | 3.3672 | 0 | 0 | 100.3327 | 97.4632 | 101493.4763 | 20 | 22.4684 | 26.5166 | 27.6579 | 90.9949 | 79.888 | 4.2 | 40 | 0.24957 | 95.1023 | 6625.0723
1396 | 3.3263 | 0 | 0 | 94.4299 | 88.1188 | 101488.2026 | 20 | 22.4352 | 26.4955 | 27.6439 | 90.783 | 80.003 | 4.2 | 40 | 0.24653 | 94.2248 | 6547.0512
1398 | 3.3273 | 0 | 0 | 94.9497 | 89.223 | 101495.4836 | 20 | 22.4402 | 26.5146 | 27.671 | 90.781 | 80.054 | 4.2 | 40 | 0.2466 | 94.5792 | 6566.4296
1400 | 3.3268 | 0 | 0 | 98.5803 | 96.8402 | 101489.7103 | 20 | 22.4352 | 26.4744 | 27.6469 | 90.9276 | 80.154 | 4.2 | 40 | 0.24657 | 93.7493 | 6496.9706
1402 | 3.3001 | 0 | 0 | 94.8594 | 90.1481 | 101486.6971 | 20 | 22.4603 | 26.4985 | 27.6388 | 91.0662 | 80.115 | 4.2 | 40 | 0.24459 | 92.9748 | 6450.4627
1404 | 3.3406 | 0 | 0 | 96.7597 | 90.5974 | 101485.9443 | 20 | 22.4734 | 26.5327 | 27.6579 | 91.2037 | 80.088 | 4.2 | 40 | 0.24759 | 94.6069 | 6568.2541
1406 | 3.3544 | 0 | 0 | 95.1683 | 93.6482 | 101492.4726 | 20 | 22.4272 | 26.5246 | 27.6418 | 91.4457 | 80.113 | 4.2 | 40 | 0.24861 | 95.8918 | 6649.2426
1408 | 3.3139 | 0 | 0 | 94.7752 | 89.4135 | 101489.9612 | 20 | 22.4242 | 26.4604 | 27.6418 | 91.3714 | 80.113 | 4.2 | 40 | 0.24561 | 93.318 | 6470.4368
1410 | 3.2873 | 0 | 0 | 99.3157 | 95.0097 | 101481.6766 | 20 | 22.4543 | 26.5196 | 27.6358 | 91.3332 | 80.181 | 4.2 | 40 | 0.24364 | 93.2352 | 6460.455
1412 | 3.3258 | 0 | 0 | 93.1822 | 89.8142 | 101495.2327 | 20 | 22.4593 | 26.5116 | 27.6519 | 91.1987 | 80.232 | 4.2 | 40 | 0.24649 | 94.0243 | 6509.9518
1414 | 3.35 | 0 | 0 | 94.8701 | 89.7087 | 101495.9877 | 20 | 22.4432 | 26.5297 | 27.6679 | 91.1093 | 80.307 | 4.2 | 40 | 0.24829 | 95.5065 | 6602.1627
1416 | 3.3006 | 0 | 0 | 99.9487 | 95.9872 | 101493.9781 | 20 | 22.4674 | 26.5216 | 27.6569 | 91.1184 | 80.23 | 4.2 | 40 | 0.24463 | 93.3587 | 6464.9886
1418 | 3.3544 | 0 | 0 | 94.4117 | 87.1998 | 101484.6875 | 20 | 22.4543 | 26.4885 | 27.6659 | 90.9999 | 80.417 | 4.2 | 40 | 0.24861 | 94.4108 | 6515.2783
1420 | 3.3139 | 0 | 0 | 96.1807 | 91.7965 | 101496.2386 | 20 | 22.5256 | 26.5799 | 27.7081 | 90.9316 | 80.549 | 4.2 | 40 | 0.24561 | 93.7355 | 6461.9147
1422 | 3.3539 | 0 | 0 | 96.3992 | 93.8956 | 101490.9649 | 20 | 22.5045 | 26.5899 | 27.6981 | 90.774 | 80.447 | 4.2 | 40 | 0.24858 | 95.5953 | 6599.3266
1424 | 3.2878 | 0 | 0 | 93.7931 | 88.7897 | 101493.2254 | 20 | 22.4694 | 26.5578 | 27.6961 | 90.8754 | 80.384 | 4.2 | 40 | 0.24368 | 93.779 | 6477.0471
1426 | 3.2863 | 0 | 0 | 99.4409 | 93.5587 | 101488.4557 | 20 | 22.4633 | 26.5257 | 27.68 | 90.9356 | 80.489 | 4.2 | 40 | 0.24357 | 93.1381 | 6420.4733
1428 | 3.3549 | 0 | 0 | 94.7896 | 92.6404 | 101494.7308 | 20 | 22.4995 | 26.5417 | 27.677 | 91.0862 | 80.525 | 4.2 | 40 | 0.24865 | 94.6126 | 6522.1406
1430 | 3.3539 | 0 | 0 | 94.1961 | 89.7929 | 101499.5027 | 20 | 22.5075 | 26.5578 | 27.7061 | 91.2138 | 80.486 | 4.2 | 40 | 0.24858 | 94.7727 | 6538.4791
1432 | 3.3263 | 0 | 0 | 99.9251 | 95.4696 | 101486.6971 | 20 | 22.4744 | 26.5548 | 27.69 | 91.4085 | 80.515 | 4.2 | 40 | 0.24653 | 94.6908 | 6525.831
1434 | 3.3243 | 0 | 0 | 93.9791 | 88.1347 | 101490.714 | 20 | 22.4332 | 26.5126 | 27.6639 | 91.271 | 80.369 | 4.2 | 40 | 0.24638 | 94.6116 | 6532.168
1436 | 3.2611 | 0 | 0 | 94.8746 | 89.3922 | 101495.4836 | 20 | 22.4824 | 26.5498 | 27.688 | 90.8844 | 80.328 | 4.2 | 40 | 0.2417 | 92.5386 | 6399.0104
1438 | 3.3268 | 0 | 0 | 98.3033 | 97.1323 | 101492.9745 | 20 | 22.4854 | 26.5367 | 27.674 | 90.7861 | 80.316 | 4.2 | 40 | 0.24657 | 94.0288 | 6503.7469
1440 | 3.3376 | 0 | 0 | 93.1997 | 88.0649 | 101486.948 | 20 | 22.4412 | 26.5709 | 27.674 | 90.6475 | 80.379 | 4.2 | 40 | 0.24737 | 96.1603 | 6638.8653
1442 | 3.3677 | 0 | 0 | 97.2492 | 90.0032 | 101493.9781 | 20 | 22.4442 | 26.5257 | 27.69 | 90.9116 | 80.308 | 4.2 | 40 | 0.2496 | 95.8952 | 6629.0351
1444 | 3.3539 | 0 | 0 | 95.7003 | 93.0487 | 101490.463 | 20 | 22.4473 | 26.5337 | 27.6609 | 90.9015 | 80.277 | 4.2 | 40 | 0.24858 | 95.6191 | 6613.8359
1446 | 3.3603 | 0 | 0 | 93.5419 | 89.8696 | 101493.9781 | 20 | 22.4694 | 26.5628 | 27.6931 | 90.7409 | 80.299 | 4.2 | 40 | 0.24905 | 95.9668 | 6637.897
1448 | 3.3287 | 0 | 0 | 100.8533 | 94.0557 | 101491.4667 | 20 | 22.4523 | 26.5467 | 27.674 | 90.5491 | 80.355 | 4.2 | 40 | 0.24671 | 95.0878 | 6568.7993
1450 | 3.3263 | 0 | 0 | 93.0487 | 89.3687 | 101493.9781 | 20 | 22.4382 | 26.5066 | 27.674 | 90.6043 | 80.316 | 4.2 | 40 | 0.24653 | 94.4113 | 6524.872
1452 | 3.3416 | 0 | 0 | 93.9624 | 88.5301 | 101498.4968 | 20 | 22.4442 | 26.5538 | 27.7031 | 90.6405 | 80.287 | 4.2 | 40 | 0.24766 | 95.8058 | 6625.2556
1454 | 3.3594 | 0 | 0 | 100.7265 | 97.574 | 101488.4557 | 20 | 22.4262 | 26.5026 | 27.6649 | 90.6184 | 80.337 | 4.2 | 40 | 0.24898 | 95.5386 | 6599.0141
1456 | 3.3811 | 0 | 0 | 93.3257 | 88.9088 | 101496.7404 | 20 | 22.4684 | 26.5467 | 27.681 | 90.5732 | 80.202 | 4.2 | 40 | 0.25059 | 96.2035 | 6665.3342
1458 | 3.3584 | 0 | 0 | 94.8101 | 88.5582 | 101500.0046 | 20 | 22.4674 | 26.5759 | 27.688 | 90.5953 | 80.181 | 4.2 | 40 | 0.24891 | 96.2634 | 6671.7939
1460 | 3.3258 | 0 | 0 | 99.976 | 96.3871 | 101490.9649 | 20 | 22.4694 | 26.5287 | 27.688 | 90.6846 | 80.202 | 4.2 | 40 | 0.24649 | 94.1874 | 6525.767
1462 | 3.3154 | 0 | 0 | 93.7985 | 87.8729 | 101488.9576 | 20 | 22.4392 | 26.5086 | 27.6609 | 90.6545 | 80.173 | 4.2 | 40 | 0.24572 | 94.1263 | 6521.3997
1464 | 3.3801 | 0 | 0 | 94.0201 | 90.0199 | 101496.4895 | 20 | 22.4774 | 26.5598 | 27.673 | 90.9075 | 80.15 | 4.2 | 40 | 0.25052 | 96.2701 | 6677.0077
1466 | 3.3208 | 0 | 0 | 98.512 | 94.7061 | 101494.9818 | 20 | 22.4764 | 26.5538 | 27.7182 | 91.0822 | 80.173 | 4.2 | 40 | 0.24613 | 94.4664 | 6549.1832
1468 | 3.3401 | 0 | 0 | 94.7919 | 87.8934 | 101496.9913 | 20 | 22.4995 | 26.5548 | 27.691 | 91.1063 | 80.075 | 4.2 | 40 | 0.24755 | 94.4992 | 6565.2371
1470 | 3.3144 | 0 | 0 | 97.9406 | 91.3851 | 101488.4557 | 20 | 22.4704 | 26.5267 | 27.679 | 90.9477 | 80.04 | 4.2 | 40 | 0.24565 | 93.7961 | 6517.0568
1472 | 3.3549 | 0 | 0 | 93.7681 | 91.7517 | 101498.4968 | 20 | 22.4844 | 26.5267 | 27.6679 | 90.7931 | 80.013 | 4.2 | 40 | 0.24865 | 94.6127 | 6578.4836
1474 | 3.3406 | 0 | 0 | 94.8116 | 90.098 | 101494.229 | 20 | 22.4945 | 26.5668 | 27.7021 | 90.7057 | 79.851 | 4.2 | 40 | 0.24759 | 94.9111 | 6619.0262
1476 | 3.3401 | 0 | 0 | 100.7614 | 96.233 | 101490.463 | 20 | 22.4975 | 26.5688 | 27.686 | 90.4537 | 79.853 | 4.2 | 40 | 0.24755 | 94.8737 | 6616.5358
1478 | 3.3149 | 0 | 0 | 93.9685 | 89.0598 | 101492.2217 | 20 | 22.4643 | 26.5397 | 27.675 | 90.4537 | 79.895 | 4.2 | 40 | 0.24569 | 94.2516 | 6564.5463
1480 | 3.3549 | 0 | 0 | 93.8372 | 90.0753 | 101498.4968 | 20 | 22.4583 | 26.5558 | 27.6639 | 90.4296 | 79.9 | 4.2 | 40 | 0.24865 | 95.9058 | 6678.4811
1482 | 3.3406 | 0 | 0 | 99.4812 | 97.3653 | 101496.9913 | 20 | 22.4975 | 26.5688 | 27.67 | 90.266 | 79.836 | 4.2 | 40 | 0.24759 | 94.8877 | 6619.4716
1484 | 3.3391 | 0 | 0 | 95.2321 | 87.5762 | 101493.2254 | 20 | 22.4995 | 26.5638 | 27.6961 | 90.1917 | 79.861 | 4.2 | 40 | 0.24748 | 94.6818 | 6602.4663
1486 | 3.3934 | 0 | 0 | 96.6262 | 90.8812 | 101497.2422 | 20 | 22.4995 | 26.5799 | 27.6941 | 90.3433 | 79.939 | 4.2 | 40 | 0.2515 | 96.6021 | 6727.2273
1488 | 3.2883 | 0 | 0 | 96.6019 | 93.6475 | 101497.4932 | 20 | 22.4724 | 26.5688 | 27.6609 | 90.3503 | 79.951 | 4.2 | 40 | 0.24371 | 93.9774 | 6539.9918
1490 | 3.3124 | 0 | 0 | 94.8184 | 89.2989 | 101496.4895 | 20 | 22.4432 | 26.5126 | 27.684 | 90.4045 | 79.857 | 4.2 | 40 | 0.2455 | 94.0421 | 6551.8872
1492 | 3.3011 | 0 | 0 | 98.1713 | 91.7593 | 101493.9781 | 20 | 22.5015 | 26.5578 | 27.7111 | 90.3664 | 79.733 | 4.2 | 40 | 0.24466 | 93.4189 | 6529.1924
1494 | 3.3011 | 0 | 0 | 92.7307 | 90.9139 | 101500.0046 | 20 | 22.5075 | 26.5638 | 27.7121 | 90.1314 | 79.636 | 4.2 | 40 | 0.24466 | 93.4188 | 6540.9654
1496 | 3.3016 | 0 | 0 | 94.6393 | 89.3907 | 101503.2687 | 20 | 22.4704 | 26.5538 | 27.7011 | 89.8282 | 79.61 | 4.2 | 40 | 0.2447 | 94.0576 | 6584.401
1498 | 3.3273 | 0 | 0 | 98.9742 | 95.6085 | 101492.9745 | 20 | 22.4553 | 26.5417 | 27.7011 | 89.9106 | 79.742 | 4.2 | 40 | 0.2466 | 94.8589 | 6623.4504
1500 | 3.3149 | 0 | 0 | 93.4615 | 87.1466 | 101499.2518 | 20 | 22.4704 | 26.5548 | 27.673 | 89.9638 | 79.803 | 4.2 | 40 | 0.24569 | 94.4606 | 6590.3542
1502 | 3.3312 | 0 | 0 | 95.6343 | 91.0687 | 101497.995 | 20 | 22.5116 | 26.5839 | 27.7212 | 89.9758 | 79.759 | 4.2 | 40 | 0.2469 | 94.6445 | 6613.0099
1504 | 3.2883 | 0 | 0 | 98.1113 | 94.7266 | 101501.0082 | 20 | 22.4734 | 26.5739 | 27.7071 | 90.0933 | 79.757 | 4.2 | 40 | 0.24371 | 94.0696 | 6568.6908
1506 | 3.3445 | 0 | 0 | 93.0031 | 87.9435 | 101497.7441 | 20 | 22.4292 | 26.5387 | 27.683 | 90.3162 | 79.825 | 4.2 | 40 | 0.24788 | 95.8908 | 6682.7707
1508 | 3.3529 | 0 | 0 | 98.0051 | 91.5142 | 101492.4726 | 20 | 22.4704 | 26.5307 | 27.6991 | 90.1676 | 79.825 | 4.2 | 40 | 0.24851 | 94.98 | 6624.0478
1510 | 3.3361 | 0 | 0 | 94.0626 | 88.9422 | 101500.5064 | 20 | 22.4955 | 26.5658 | 27.6941 | 90.0672 | 79.793 | 4.2 | 40 | 0.24726 | 94.7381 | 6613.7669
1512 | 3.3539 | 0 | 0 | 92.2935 | 88.9604 | 101495.9877 | 20 | 22.4643 | 26.5467 | 27.681 | 90.2208 | 79.832 | 4.2 | 40 | 0.24858 | 95.525 | 6660.5479
1514 | 3.306 | 0 | 0 | 99.7673 | 97.36 | 101495.4836 | 20 | 22.4453 | 26.5387 | 27.689 | 90.4246 | 79.806 | 4.2 | 40 | 0.24503 | 94.4159 | 6584.0076
1516 | 3.3431 | 0 | 0 | 94.7167 | 88.2994 | 101489.2085 | 20 | 22.4422 | 26.5086 | 27.6418 | 90.5531 | 79.726 | 4.2 | 40 | 0.24777 | 94.8409 | 6622.53
1518 | 3.3845 | 0 | 0 | 93.1185 | 87.6999 | 101497.7441 | 20 | 22.5126 | 26.5518 | 27.6971 | 90.5963 | 79.576 | 4.2 | 40 | 0.25085 | 95.3766 | 6685.657
1520 | 3.2868 | 0 | 0 | 96.2733 | 94.9421 | 101502.2628 | 20 | 22.5025 | 26.5478 | 27.681 | 90.4507 | 79.458 | 4.2 | 40 | 0.2436 | 92.7603 | 6514.5805
1522 | 3.3524 | 0 | 0 | 95.4248 | 89.7186 | 101499.2518 | 20 | 22.4834 | 26.5719 | 27.6951 | 90.2509 | 79.402 | 4.2 | 40 | 0.24847 | 95.6236 | 6720.0288
1524 | 3.3406 | 0 | 0 | 98.8733 | 92.289 | 101489.9612 | 20 | 22.4493 | 26.5377 | 27.674 | 90.009 | 79.398 | 4.2 | 40 | 0.24759 | 95.2858 | 6692.7449
1526 | 3.3401 | 0 | 0 | 93.0547 | 88.584 | 101497.995 | 20 | 22.4864 | 26.5297 | 27.676 | 89.8563 | 79.447 | 4.2 | 40 | 0.24755 | 94.2184 | 6616.3956
1528 | 3.3139 | 0 | 0 | 93.0001 | 88.6508 | 101499.2518 | 20 | 22.5226 | 26.5668 | 27.689 | 89.9286 | 79.423 | 4.2 | 40 | 0.24561 | 93.5033 | 6573.1234
1530 | 3.3401 | 0 | 0 | 98.5485 | 96.3461 | 101493.9781 | 20 | 22.4975 | 26.5668 | 27.676 | 89.8734 | 79.415 | 4.2 | 40 | 0.24755 | 94.8269 | 6664.1627
1532 | 3.3317 | 0 | 0 | 94.2895 | 87.366 | 101497.7441 | 20 | 22.4533 | 26.5317 | 27.67 | 89.9447 | 79.498 | 4.2 | 40 | 0.24693 | 94.7989 | 6647.3418
1534 | 3.3011 | 0 | 0 | 93.7066 | 88.3328 | 101500.5064 | 20 | 22.4975 | 26.5076 | 27.679 | 90.0612 | 79.453 | 4.2 | 40 | 0.24466 | 92.3548 | 6486.1013
1536 | 3.3095 | 0 | 0 | 96.5222 | 93.6042 | 101500.7573 | 20 | 22.5316 | 26.5588 | 27.6579 | 90.1284 | 79.574 | 4.2 | 40 | 0.24529 | 92.9837 | 6520.3272
1538 | 3.3149 | 0 | 0 | 93.3621 | 89.922 | 101496.7404 | 20 | 22.5075 | 26.5658 | 27.6971 | 90.1144 | 79.541 | 4.2 | 40 | 0.24569 | 93.8565 | 6582.5544
1540 | 3.3268 | 0 | 0 | 98.0825 | 90.7871 | 101493.9781 | 20 | 22.4684 | 26.5357 | 27.691 | 90.2108 | 79.614 | 4.2 | 40 | 0.24657 | 94.4019 | 6607.8114
1542 | 3.311 | 0 | 0 | 93.6634 | 90.5685 | 101504.7742 | 20 | 22.4623 | 26.5136 | 27.6679 | 90.4387 | 79.721 | 4.2 | 40 | 0.2454 | 93.5824 | 6537.5189
1544 | 3.2873 | 0 | 0 | 94.1513 | 88.307 | 101501.51 | 20 | 22.5065 | 26.5688 | 27.7001 | 90.7087 | 79.801 | 4.2 | 40 | 0.24364 | 93.1659 | 6504.3526
1546 | 3.3668 | 0 | 0 | 98.8649 | 96.7544 | 101501.0082 | 20 | 22.4985 | 26.5558 | 27.689 | 90.7569 | 79.85 | 4.2 | 40 | 0.24953 | 95.3006 | 6646.7742
1548 | 3.3218 | 0 | 0 | 95.3747 | 88.7889 | 101496.7404 | 20 | 22.4794 | 26.5739 | 27.6951 | 90.8674 | 79.899 | 4.2 | 40 | 0.2462 | 94.8902 | 6610.3017
1550 | 3.3046 | 0 | 0 | 95.0074 | 88.1932 | 101506.2797 | 20 | 22.4734 | 26.5317 | 27.676 | 90.8503 | 79.838 | 4.2 | 40 | 0.24492 | 93.5631 | 6524.0952
1552 | 3.2868 | 0 | 0 | 97.3813 | 95.0264 | 101502.5137 | 20 | 22.5015 | 26.5688 | 27.687 | 90.5642 | 79.675 | 4.2 | 40 | 0.2436 | 93.267 | 6525.1902
1554 | 3.3134 | 0 | 0 | 93.9495 | 90.29 | 101501.2591 | 20 | 22.4734 | 26.5638 | 27.6951 | 90.3292 | 79.611 | 4.2 | 40 | 0.24558 | 94.5576 | 6619.6391
1556 | 3.2863 | 0 | 0 | 98.2259 | 88.3275 | 101497.4932 | 20 | 22.4593 | 26.5608 | 27.684 | 89.8684 | 79.692 | 4.2 | 40 | 0.24357 | 94.0362 | 6572.2011
1558 | 3.3396 | 0 | 0 | 94.2606 | 90.8736 | 101504.0214 | 20 | 22.4653 | 26.5528 | 27.681 | 89.7409 | 79.728 | 4.2 | 40 | 0.24752 | 95.2342 | 6652.446
1560 | 3.3801 | 0 | 0 | 93.4547 | 90.0904 | 101499.2518 | 20 | 22.4653 | 26.5046 | 27.6649 | 89.4698 | 79.809 | 4.2 | 40 | 0.25052 | 95.2517 | 6644.2699
1562 | 3.2873 | 0 | 0 | 99.8932 | 95.8718 | 101496.2386 | 20 | 22.4794 | 26.5498 | 27.6649 | 89.4698 | 79.87 | 4.2 | 40 | 0.24364 | 93.3503 | 6506.311
1564 | 3.3001 | 0 | 0 | 93.9472 | 89.201 | 101500.7573 | 20 | 22.4814 | 26.5558 | 27.6679 | 89.8634 | 79.894 | 4.2 | 40 | 0.24459 | 93.8072 | 6535.6576
1566 | 3.3263 | 0 | 0 | 94.0572 | 89.0196 | 101499.7536 | 20 | 22.4814 | 26.5488 | 27.687 | 90.1194 | 79.972 | 4.2 | 40 | 0.24653 | 94.3878 | 6567.1812
1568 | 3.2828 | 0 | 0 | 99.1852 | 98.1273 | 101496.9913 | 20 | 22.4493 | 26.5387 | 27.672 | 90.1335 | 80.002 | 4.2 | 40 | 0.24331 | 93.6612 | 6509.5917
1570 | 3.3406 | 0 | 0 | 94.8602 | 89.922 | 101492.9745 | 20 | 22.4523 | 26.5397 | 27.682 | 89.9608 | 79.96 | 4.2 | 40 | 0.24759 | 95.2624 | 6626.061
1572 | 3.2873 | 0 | 0 | 94.2136 | 89.8013 | 101496.9913 | 20 | 22.5035 | 26.5779 | 27.7111 | 89.9939 | 79.993 | 4.2 | 40 | 0.24364 | 93.4423 | 6501.5225
1574 | 3.3559 | 0 | 0 | 98.1455 | 95.7299 | 101504.7742 | 20 | 22.5136 | 26.5799 | 27.6951 | 89.9698 | 79.854 | 4.2 | 40 | 0.24872 | 95.2047 | 6641.363
1576 | 3.3144 | 0 | 0 | 93.8956 | 89.5061 | 101497.2422 | 20 | 22.4774 | 26.5558 | 27.682 | 88.4457 | 79.83 | 4.2 | 40 | 0.24565 | 94.3071 | 6577.3525
1578 | 3.3233 | 0 | 0 | 98.6957 | 91.7183 | 101492.9745 | 20 | 22.5065 | 26.5859 | 27.6931 | 88.772 | 79.925 | 4.2 | 40 | 0.24631 | 94.5832 | 6589.0405
1580 | 3.3001 | 0 | 0 | 94.6651 | 88.3305 | 101497.4932 | 20 | 22.5186 | 26.596 | 27.7111 | 89.1365 | 79.944 | 4.2 | 40 | 0.24459 | 93.8764 | 6539.0179
1582 | 3.3416 | 0 | 0 | 94.8435 | 88.6994 | 101498.4968 | 20 | 22.5256 | 26.5889 | 27.7101 | 89.259 | 79.928 | 4.2 | 40 | 0.24766 | 94.7283 | 6600.9986
1584 | 3.3648 | 0 | 0 | 100.8927 | 97.8867 | 101493.9781 | 20 | 22.4925 | 26.5769 | 27.7011 | 89.3353 | 79.97 | 4.2 | 40 | 0.24938 | 95.8813 | 6672.6143
1586 | 3.3682 | 0 | 0 | 95.6935 | 88.8473 | 101491.4667 | 20 | 22.4744 | 26.5337 | 27.69 | 89.6455 | 79.958 | 4.2 | 40 | 0.24964 | 95.3898 | 6637.7047
1588 | 3.2591 | 0 | 0 | 94.8685 | 88.3601 | 101496.4895 | 20 | 22.5075 | 26.596 | 27.7172 | 89.7057 | 79.941 | 4.2 | 40 | 0.24155 | 92.962 | 6474.4166
1590 | 3.3268 | 0 | 0 | 97.8708 | 97.2477 | 101500.7573 | 20 | 22.4935 | 26.5799 | 27.685 | 89.7248 | 79.826 | 4.2 | 40 | 0.24657 | 94.8447 | 6617.1662
1592 | 3.3278 | 0 | 0 | 96.3142 | 90.8015 | 101491.9708 | 20 | 22.4684 | 26.5749 | 27.7041 | 89.9216 | 79.909 | 4.2 | 40 | 0.24664 | 95.3394 | 6639.1574
1594 | 3.3406 | 0 | 0 | 97.401 | 91.1772 | 101495.7368 | 20 | 22.4663 | 26.5427 | 27.7011 | 90.0612 | 79.839 | 4.2 | 40 | 0.24759 | 95.0048 | 6623.7027
1596 | 3.3268 | 0 | 0 | 94.9831 | 92.5933 | 101496.9913 | 20 | 22.5206 | 26.5859 | 27.687 | 90.1887 | 79.787 | 4.2 | 40 | 0.24657 | 94.355 | 6590.6037
1598 | 3.3406 | 0 | 0 | 94.2902 | 90.4585 | 101495.9877 | 20 | 22.5015 | 26.5749 | 27.6981 | 90.279 | 79.685 | 4.2 | 40 | 0.24759 | 94.9345 | 6640.6899
1600 | 3.3139 | 0 | 0 | 101.0324 | 93.3522 | 101488.9576 | 20 | 22.4493 | 26.5397 | 27.682 | 90.1214 | 79.675 | 4.2 | 40 | 0.24561 | 94.5719 | 6610.4442
1602 | 3.3416 | 0 | 0 | 93.8592 | 89.5562 | 101505.0251 | 20 | 22.4463 | 26.5377 | 27.687 | 89.9648 | 79.558 | 4.2 | 40 | 0.24766 | 95.3843 | 6680.536
1604 | 3.3149 | 0 | 0 | 95.1235 | 89.5607 | 101499.2518 | 20 | 22.5186 | 26.5749 | 27.69 | 89.9166 | 79.58 | 4.2 | 40 | 0.24569 | 93.81 | 6576.07
1606 | 3.3539 | 0 | 0 | 100.4473 | 98.5523 | 101496.9913 | 20 | 22.4824 | 26.5698 | 27.687 | 89.8975 | 79.614 | 4.2 | 40 | 0.24858 | 95.6424 | 6696.2925
1608 | 3.3544 | 0 | 0 | 95.2837 | 89.5691 | 101494.7308 | 20 | 22.4442 | 26.5267 | 27.677 | 89.9166 | 79.57 | 4.2 | 40 | 0.24861 | 95.5391 | 6689.7399
1610 | 3.3544 | 0 | 0 | 95.4172 | 90.2673 | 101498.2459 | 20 | 22.4412 | 26.5377 | 27.669 | 89.9919 | 79.702 | 4.2 | 40 | 0.24861 | 95.8682 | 6696.9554
1612 | 3.3692 | 0 | 0 | 97.9284 | 96.6983 | 101503.0178 | 20 | 22.4905 | 26.5588 | 27.679 | 89.9798 | 79.67 | 4.2 | 40 | 0.24971 | 95.6302 | 6689.8191
1614 | 3.3416 | 0 | 0 | 95.5963 | 90.7074 | 101496.7404 | 20 | 22.4663 | 26.5347 | 27.671 | 90.0692 | 79.763 | 4.2 | 40 | 0.24766 | 94.8456 | 6621.372
1616 | 3.3273 | 0 | 0 | 96.3704 | 90.2809 | 101498.4968 | 20 | 22.4985 | 26.5658 | 27.687 | 90.4166 | 79.916 | 4.2 | 40 | 0.2466 | 94.4157 | 6577.4866
1618 | 3.3411 | 0 | 0 | 97.1126 | 95.5849 | 101501.51 | 20 | 22.4935 | 26.5779 | 27.674 | 90.6154 | 80.053 | 4.2 | 40 | 0.24763 | 95.206 | 6616.1766
1620 | 3.2739 | 0 | 0 | 94.9991 | 90.8782 | 101498.4968 | 20 | 22.4513 | 26.5508 | 27.6679 | 90.7379 | 80.051 | 4.2 | 40 | 0.24265 | 93.6371 | 6502.6089
1622 | 3.3411 | 0 | 0 | 100.7114 | 93.0031 | 101495.4836 | 20 | 22.4824 | 26.5488 | 27.685 | 90.6987 | 79.99 | 4.2 | 40 | 0.24763 | 94.7846 | 6592.8446
1624 | 3.3549 | 0 | 0 | 94.6469 | 88.5749 | 101499.5027 | 20 | 22.5387 | 26.5709 | 27.7131 | 90.5531 | 80.026 | 4.2 | 40 | 0.24865 | 94.3773 | 6566.8285
1626 | 3.2892 | 0 | 0 | 94.7623 | 90.0517 | 101501.2591 | 20 | 22.5306 | 26.608 | 27.7232 | 90.5411 | 79.943 | 4.2 | 40 | 0.24379 | 93.5675 | 6518.9773
1628 | 3.2473 | 0 | 0 | 100.7561 | 98.1918 | 101500.0046 | 20 | 22.4975 | 26.6191 | 27.7192 | 90.3493 | 79.96 | 4.2 | 40 | 0.24067 | 93.3751 | 6499.8942
1630 | 3.3149 | 0 | 0 | 94.5505 | 88.1522 | 101498.7477 | 20 | 22.4955 | 26.5608 | 27.7141 | 90.523 | 79.929 | 4.2 | 40 | 0.24569 | 94.0191 | 6548.0318
1632 | 3.3278 | 0 | 0 | 96.6429 | 90.2521 | 101505.276 | 20 | 22.5437 | 26.595 | 27.7312 | 90.7027 | 80.042 | 4.2 | 40 | 0.24664 | 94.0565 | 6543.2536
1634 | 3.3154 | 0 | 0 | 99.6428 | 96.6451 | 101507.2856 | 20 | 22.5387 | 26.605 | 27.7101 | 90.8202 | 80.054 | 4.2 | 40 | 0.24572 | 94.0561 | 6541.2903
1636 | 3.2804 | 0 | 0 | 95.0651 | 89.56 | 101496.9913 | 20 | 22.4915 | 26.5729 | 27.7262 | 90.8995 | 80.051 | 4.2 | 40 | 0.24313 | 93.4067 | 6491.1379
1638 | 3.3139 | 0 | 0 | 98.6904 | 90.4259 | 101491.4667 | 20 | 22.4744 | 26.5618 | 27.7232 | 90.6806 | 80.112 | 4.2 | 40 | 0.24561 | 94.5021 | 6558.3625
1640 | 3.3406 | 0 | 0 | 94.3145 | 94.0747 | 101497.2422 | 20 | 22.5055 | 26.5859 | 27.7121 | 90.3694 | 79.954 | 4.2 | 40 | 0.24759 | 95.0983 | 6621.4676
1642 | 3.3282 | 0 | 0 | 94.2963 | 90.0358 | 101498.4968 | 20 | 22.5186 | 26.608 | 27.7151 | 90.2349 | 79.89 | 4.2 | 40 | 0.24668 | 94.9567 | 6620.4917
1644 | 3.3682 | 0 | 0 | 101.4338 | 97.0656 | 101496.4895 | 20 | 22.5327 | 26.6 | 27.7041 | 90.1676 | 79.868 | 4.2 | 40 | 0.24964 | 95.5784 | 6668.0235
1646 | 3.3129 | 0 | 0 | 94.4678 | 87.9222 | 101494.7308 | 20 | 22.4724 | 26.5407 | 27.6991 | 90.2158 | 79.937 | 4.2 | 40 | 0.24554 | 94.0328 | 6545.4427
1648 | 3.3411 | 0 | 0 | 93.0707 | 91.4709 | 101501.51 | 20 | 22.4804 | 26.5598 | 27.677 | 90.3523 | 79.971 | 4.2 | 40 | 0.24763 | 95.089 | 6615.9699
1650 | 3.3401 | 0 | 0 | 99.6071 | 95.9075 | 101498.9986 | 20 | 22.5176 | 26.5929 | 27.7081 | 90.4598 | 79.901 | 4.2 | 40 | 0.24755 | 94.9672 | 6619.8375
1652 | 3.3154 | 0 | 0 | 93.378 | 89.4112 | 101497.2422 | 20 | 22.5176 | 26.5739 | 27.7001 | 90.3644 | 79.945 | 4.2 | 40 | 0.24572 | 93.8239 | 6535.1277
1654 | 3.3006 | 0 | 0 | 97.4556 | 93.2096 | 101493.2254 | 20 | 22.4874 | 26.5478 | 27.671 | 90.3543 | 79.855 | 4.2 | 40 | 0.24463 | 93.4974 | 6519.1826
1656 | 3.2927 | 0 | 0 | 97.2325 | 90.035 | 101504.7742 | 20 | 22.4563 | 26.5287 | 27.671 | 90.3041 | 79.931 | 4.2 | 40 | 0.24404 | 93.5507 | 6510.7405
1658 | 3.3406 | 0 | 0 | 94.5513 | 88.244 | 101502.7669 | 20 | 22.5206 | 26.5739 | 27.692 | 90.4336 | 79.989 | 4.2 | 40 | 0.24759 | 94.4662 | 6575.1745
1660 | 3.3672 | 0 | 0 | 99.3142 | 97.9983 | 101495.4836 | 20 | 22.5005 | 26.5658 | 27.681 | 90.4316 | 79.913 | 4.2 | 40 | 0.24957 | 95.5033 | 6653.8334
1662 | 3.3268 | 0 | 0 | 95.1964 | 89.138 | 101496.9913 | 20 | 22.4442 | 26.5407 | 27.681 | 90.529 | 79.936 | 4.2 | 40 | 0.24657 | 95.0781 | 6615.0749
1664 | 3.3396 | 0 | 0 | 95.2943 | 89.5873 | 101500.0046 | 20 | 22.4694 | 26.5257 | 27.6639 | 90.7047 | 79.863 | 4.2 | 40 | 0.24752 | 94.5087 | 6586.7027
1666 | 3.3011 | 0 | 0 | 99.2186 | 97.146 | 101501.7609 | 20 | 22.5065 | 26.5628 | 27.687 | 90.7489 | 79.764 | 4.2 | 40 | 0.24466 | 93.4188 | 6526.2285
1668 | 3.3282 | 0 | 0 | 95.3398 | 90.3037 | 101496.9913 | 20 | 22.4975 | 26.5739 | 27.7091 | 90.4206 | 79.643 | 4.2 | 40 | 0.24668 | 94.6536 | 6625.448
1670 | 3.3391 | 0 | 0 | 98.6023 | 90.5109 | 101495.4836 | 20 | 22.4483 | 26.5357 | 27.683 | 90.279 | 79.67 | 4.2 | 40 | 0.24748 | 95.2202 | 6656.229
1672 | 3.3287 | 0 | 0 | 95.2321 | 90.9237 | 101502.0119 | 20 | 22.4684 | 26.5216 | 27.7031 | 90.1505 | 79.589 | 4.2 | 40 | 0.24671 | 94.1314 | 6591.7607
1674 | 3.3534 | 0 | 0 | 93.6603 | 90.2179 | 101496.9913 | 20 | 22.4754 | 26.5387 | 27.687 | 90.2579 | 79.549 | 4.2 | 40 | 0.24854 | 95.0644 | 6662.5788
1676 | 3.2888 | 0 | 0 | 100.9739 | 98.3398 | 101497.4932 | 20 | 22.4995 | 26.5598 | 27.7081 | 90.1776 | 79.514 | 4.2 | 40 | 0.24375 | 93.1617 | 6536.002
1678 | 3.2868 | 0 | 0 | 95.7754 | 89.9728 | 101496.2386 | 20 | 22.4965 | 26.5839 | 27.6971 | 89.8001 | 79.427 | 4.2 | 40 | 0.2436 | 93.7276 | 6585.4056
1680 | 3.3016 | 0 | 0 | 93.523 | 89.6859 | 101499.2518 | 20 | 22.5146 | 26.5789 | 27.7161 | 89.6274 | 79.42 | 4.2 | 40 | 0.2447 | 93.6178 | 6580.5872
1682 | 3.3544 | 0 | 0 | 98.6562 | 97.7767 | 101498.7477 | 20 | 22.4965 | 26.5618 | 27.6931 | 89.8513 | 79.523 | 4.2 | 40 | 0.24861 | 95.1393 | 6673.3358
1684 | 3.3401 | 0 | 0 | 95.9325 | 90.7879 | 101495.4836 | 20 | 22.4925 | 26.5658 | 27.684 | 90.283 | 79.621 | 4.2 | 40 | 0.24755 | 94.9205 | 6646.1032
1686 | 3.2991 | 0 | 0 | 94.6166 | 90.3014 | 101501.2591 | 20 | 22.5497 | 26.595 | 27.7182 | 90.3292 | 79.606 | 4.2 | 40 | 0.24452 | 93.1084 | 6527.4811
1688 | 3.3539 | 0 | 0 | 97.2029 | 96.5427 | 101502.2628 | 20 | 22.5196 | 26.5789 | 27.6971 | 90.4276 | 79.506 | 4.2 | 40 | 0.24858 | 94.9842 | 6667.1481
1690 | 3.2868 | 0 | 0 | 95.0613 | 90.9359 | 101495.9877 | 20 | 22.4754 | 26.5498 | 27.7081 | 90.3814 | 79.484 | 4.2 | 40 | 0.2436 | 93.4283 | 6555.3828
1692 | 3.3411 | 0 | 0 | 99.7794 | 93.1587 | 101494.7308 | 20 | 22.4925 | 26.5417 | 27.678 | 90.276 | 79.472 | 4.2 | 40 | 0.24763 | 94.3866 | 6625.9988
1694 | 3.3322 | 0 | 0 | 95.3254 | 89.9857 | 101498.4968 | 20 | 22.5276 | 26.5789 | 27.7051 | 89.9708 | 79.469 | 4.2 | 40 | 0.24697 | 94.1821 | 6616.0767
1696 | 3.3529 | 0 | 0 | 93.5799 | 89.8931 | 101503.0178 | 20 | 22.4925 | 26.5709 | 27.6941 | 89.8413 | 79.426 | 4.2 | 40 | 0.24851 | 95.4028 | 6702.7473
1698 | 3.3361 | 0 | 0 | 100.1027 | 97.9102 | 101494.9818 | 20 | 22.4834 | 26.5518 | 27.689 | 89.76 | 79.465 | 4.2 | 40 | 0.24726 | 94.6914 | 6647.16
1700 | 3.3006 | 0 | 0 | 95.7208 | 87.2377 | 101497.995 | 20 | 22.5025 | 26.5387 | 27.678 | 90.025 | 79.548 | 4.2 | 40 | 0.24463 | 92.9422 | 6517.0618
1702 | 3.3273 | 0 | 0 | 94.0626 | 89.7527 | 101503.2687 | 20 | 22.5196 | 26.604 | 27.7262 | 89.9708 | 79.596 | 4.2 | 40 | 0.2466 | 94.812 | 6644.5653
1704 | 3.3544 | 0 | 0 | 99.0524 | 96.7916 | 101496.7404 | 20 | 22.5045 | 26.5859 | 27.7232 | 90.2911 | 79.648 | 4.2 | 40 | 0.24861 | 95.5153 | 6686
1706 | 3.3529 | 0 | 0 | 95.9834 | 89.2989 | 101493.7272 | 20 | 22.5095 | 26.5799 | 27.7121 | 90.3684 | 79.517 | 4.2 | 40 | 0.24851 | 95.2147 | 6680.8617
1708 | 3.3391 | 0 | 0 | 97.3623 | 90.3758 | 101494.4799 | 20 | 22.5035 | 26.5608 | 27.6971 | 90.5411 | 79.624 | 4.2 | 40 | 0.24748 | 94.518 | 6618.8543
1710 | 3.344 | 0 | 0 | 93.3386 | 93.372 | 101495.7368 | 20 | 22.5246 | 26.5779 | 27.7011 | 90.4869 | 79.707 | 4.2 | 40 | 0.24785 | 94.5639 | 6614.895
1712 | 3.3149 | 0 | 0 | 94.7251 | 89.6366 | 101500.7573 | 20 | 22.5025 | 26.597 | 27.7252 | 90.3292 | 79.7 | 4.2 | 40 | 0.24569 | 94.6927 | 6622.1603
1714 | 3.3544 | 0 | 0 | 99.7536 | 95.012 | 101493.7272 | 20 | 22.4804 | 26.5568 | 27.6991 | 90.7469 | 79.814 | 4.2 | 40 | 0.24861 | 95.3979 | 6655.6383
1716 | 3.3001 | 0 | 0 | 94.6682 | 89.1942 | 101495.9877 | 20 | 22.4744 | 26.5437 | 27.68 | 90.8302 | 79.936 | 4.2 | 40 | 0.24459 | 93.6916 | 6522.034
1718 | 3.3539 | 0 | 0 | 94.0603 | 90.7363 | 101501.0082 | 20 | 22.5075 | 26.5678 | 27.685 | 90.8182 | 80.051 | 4.2 | 40 | 0.24858 | 95.0078 | 6604.2437
1720 | 3.3549 | 0 | 0 | 99.0418 | 95.5576 | 101494.4799 | 20 | 22.5246 | 26.5809 | 27.7172 | 90.9909 | 80.038 | 4.2 | 40 | 0.24865 | 94.9416 | 6603.0978
1722 | 3.3001 | 0 | 0 | 94.889 | 88.6333 | 101494.229 | 20 | 22.5075 | 26.5698 | 27.7041 | 90.9889 | 80.034 | 4.2 | 40 | 0.24459 | 93.5296 | 6503.4156
1724 | 3.3134 | 0 | 0 | 95.5455 | 91.1294 | 101496.7404 | 20 | 22.4543 | 26.5478 | 27.689 | 91.0591 | 80.118 | 4.2 | 40 | 0.24558 | 94.6273 | 6564.0836
1726 | 3.2962 | 0 | 0 | 97.4503 | 93.4608 | 101498.4968 | 20 | 22.4955 | 26.5387 | 27.677 | 91.3995 | 80.139 | 4.2 | 40 | 0.2443 | 92.9789 | 6451.9906
1728 | 3.3411 | 0 | 0 | 95.5402 | 89.7383 | 101501.7609 | 20 | 22.5206 | 26.602 | 27.7262 | 91.5782 | 80.223 | 4.2 | 40 | 0.24763 | 95.1356 | 6594.9168
1730 | 3.3011 | 0 | 0 | 98.7731 | 93.0479 | 101488.2026 | 20 | 22.5126 | 26.5829 | 27.7061 | 91.7017 | 80.266 | 4.2 | 40 | 0.24466 | 93.7426 | 6492.6107
1732 | 3.3159 | 0 | 0 | 93.0084 | 89.9189 | 101495.4836 | 20 | 22.4955 | 26.5668 | 27.7061 | 91.9316 | 80.256 | 4.2 | 40 | 0.24576 | 94.1866 | 6522.556
1734 | 3.3016 | 0 | 0 | 96.1693 | 89.5698 | 101499.2518 | 20 | 22.4844 | 26.5638 | 27.7272 | 91.9698 | 80.185 | 4.2 | 40 | 0.2447 | 93.965 | 6513.971
1736 | 3.3268 | 0 | 0 | 99.4091 | 98.1326 | 101490.9649 | 20 | 22.4925 | 26.5558 | 27.7061 | 91.7559 | 80.207 | 4.2 | 40 | 0.24657 | 94.3085 | 6536.2081
1738 | 3.3164 | 0 | 0 | 93.9965 | 90.1906 | 101490.9649 | 20 | 22.5236 | 26.5929 | 27.692 | 91.3262 | 80.222 | 4.2 | 40 | 0.2458 | 94.1539 | 6527.3163
1740 | 3.3282 | 0 | 0 | 94.2067 | 89.8886 | 101497.995 | 20 | 22.4925 | 26.5929 | 27.7352 | 91.0029 | 80.197 | 4.2 | 40 | 0.24668 | 95.2134 | 6600.0643
1742 | 3.3001 | 0 | 0 | 99.8045 | 96.1139 | 101498.9986 | 20 | 22.5055 | 26.5698 | 27.7151 | 90.771 | 80.102 | 4.2 | 40 | 0.24459 | 93.5759 | 6498.7233
1744 | 3.3115 | 0 | 0 | 93.4873 | 89.5994 | 101494.4799 | 20 | 22.4613 | 26.5297 | 27.7121 | 90.4517 | 80.015 | 4.2 | 40 | 0.24543 | 93.9909 | 6532.4006
1746 | 3.2902 | 0 | 0 | 94.0519 | 91.6902 | 101502.0119 | 20 | 22.5327 | 26.5889 | 27.7232 | 90.0481 | 79.933 | 4.2 | 40 | 0.24386 | 93.1112 | 6488.5495
1748 | 3.3287 | 0 | 0 | 97.4951 | 92.632 | 101501.51 | 20 | 22.5316 | 26.598 | 27.7151 | 89.9758 | 79.855 | 4.2 | 40 | 0.24671 | 94.4343 | 6589.5896
1750 | 3.2888 | 0 | 0 | 93.3006 | 89.1448 | 101500.5064 | 20 | 22.5296 | 26.5759 | 27.7272 | 89.9808 | 79.938 | 4.2 | 40 | 0.24375 | 92.8389 | 6468.6706
1752 | 3.2744 | 0 | 0 | 100.2226 | 96.0904 | 101496.2386 | 20 | 22.4885 | 26.5648 | 27.692 | 90.0511 | 79.86 | 4.2 | 40 | 0.24269 | 93.1234 | 6492.6532
1754 | 3.3001 | 0 | 0 | 95.7223 | 88.581 | 101498.9986 | 20 | 22.5055 | 26.5709 | 27.6991 | 90.1826 | 79.817 | 4.2 | 40 | 0.24459 | 93.599 | 6532.6543
1756 | 3.2883 | 0 | 0 | 92.5956 | 89.0439 | 101503.7705 | 20 | 22.5497 | 26.5899 | 27.7232 | 90.1686 | 79.795 | 4.2 | 40 | 0.24371 | 92.6867 | 6476.4635
1758 | 3.3352 | 0 | 0 | 99.3256 | 97.5763 | 101494.7308 | 20 | 22.5276 | 26.5739 | 27.7131 | 89.7941 | 79.747 | 4.2 | 40 | 0.24719 | 94.149 | 6581.6183
1760 | 3.3046 | 0 | 0 | 94.6795 | 88.1727 | 101491.9708 | 20 | 22.4704 | 26.5357 | 27.6971 | 90.0411 | 79.829 | 4.2 | 40 | 0.24492 | 93.7252 | 6536.0809
1762 | 3.3282 | 0 | 0 | 96.7506 | 89.7633 | 101500.7573 | 20 | 22.5367 | 26.5628 | 27.678 | 90.267 | 79.788 | 4.2 | 40 | 0.24668 | 93.4874 | 6531.716
1764 | 3.3021 | 0 | 0 | 98.3466 | 94.675 | 101502.0119 | 20 | 22.5166 | 26.5869 | 27.7131 | 90.2841 | 79.776 | 4.2 | 40 | 0.24474 | 93.7707 | 6550.5852
1766 | 3.3001 | 0 | 0 | 93.501 | 90.3674 | 101497.4932 | 20 | 22.5005 | 26.5709 | 27.7262 | 90.1234 | 79.669 | 4.2 | 40 | 0.24459 | 93.7147 | 6557.0841
1768 | 3.3016 | 0 | 0 | 100.2613 | 93.5169 | 101493.2254 | 20 | 22.4834 | 26.5578 | 27.691 | 90.1184 | 79.644 | 4.2 | 40 | 0.2447 | 93.8493 | 6567.4138
1770 | 3.3411 | 0 | 0 | 93.4319 | 89.0644 | 101496.7404 | 20 | 22.4643 | 26.5226 | 27.678 | 90.0561 | 79.613 | 4.2 | 40 | 0.24763 | 94.5974 | 6621.1468
1772 | 3.2734 | 0 | 0 | 93.9146 | 89.5258 | 101495.2327 | 20 | 22.5196 | 26.5929 | 27.7051 | 90.0702 | 79.613 | 4.2 | 40 | 0.24261 | 93.0263 | 6517.4844
1774 | 3.2868 | 0 | 0 | 100.4085 | 97.6917 | 101497.7441 | 20 | 22.4895 | 26.5739 | 27.683 | 90.2047 | 79.686 | 4.2 | 40 | 0.2436 | 93.6586 | 6549.9458
1776 | 3.2883 | 0 | 0 | 93.5404 | 88.7525 | 101492.2217 | 20 | 22.4744 | 26.5508 | 27.7141 | 90.1214 | 79.708 | 4.2 | 40 | 0.24371 | 93.5166 | 6535.7803
1778 | 3.3534 | 0 | 0 | 94.7995 | 88.8466 | 101495.9877 | 20 | 22.4945 | 26.5377 | 27.6951 | 90.2579 | 79.71 | 4.2 | 40 | 0.24854 | 94.5943 | 6613.1909
1780 | 3.3539 | 0 | 0 | 96.2786 | 95.2169 | 101500.0046 | 20 | 22.5437 | 26.6161 | 27.7232 | 90.2429 | 79.66 | 4.2 | 40 | 0.24858 | 95.2896 | 6673.3752
1782 | 3.3036 | 0 | 0 | 94.2986 | 89.5918 | 101498.2459 | 20 | 22.5045 | 26.594 | 27.7282 | 90.2218 | 79.5 | 4.2 | 40 | 0.24485 | 94.2526 | 6614.741
1784 | 3.3144 | 0 | 0 | 97.4845 | 90.5207 | 101490.714 | 20 | 22.5236 | 26.5648 | 27.69 | 90.1094 | 79.619 | 4.2 | 40 | 0.24565 | 93.4475 | 6546.7645
1786 | 3.2769 | 0 | 0 | 93.1041 | 93.0176 | 101502.7669 | 20 | 22.4905 | 26.5216 | 27.68 | 90.2057 | 79.6 | 4.2 | 40 | 0.24287 | 92.1602 | 6454.9798
1788 | 3.3984 | 0 | 0 | 94.9239 | 89.8362 | 101501.2591 | 20 | 22.5156 | 26.5889 | 27.68 | 90.1184 | 79.569 | 4.2 | 40 | 0.25187 | 96.576 | 6770.9138
1790 | 3.2878 | 0 | 0 | 100.5224 | 95.629 | 101498.7477 | 20 | 22.5276 | 26.5678 | 27.7021 | 90.282 | 79.679 | 4.2 | 40 | 0.24368 | 92.6728 | 6486.1326
1792 | 3.3149 | 0 | 0 | 93.1678 | 89.8833 | 101501.2591 | 20 | 22.5085 | 26.5709 | 27.6981 | 90.1495 | 79.689 | 4.2 | 40 | 0.24569 | 93.9494 | 6572.132
1794 | 3.2744 | 0 | 0 | 94.5983 | 88.5408 | 101501.2591 | 20 | 22.5095 | 26.5879 | 27.7262 | 89.7258 | 79.649 | 4.2 | 40 | 0.24269 | 93.1692 | 6522.2317
1796 | 3.2848 | 0 | 0 | 98.912 | 96.3522 | 101496.9913 | 20 | 22.4985 | 26.5518 | 27.7011 | 89.7409 | 79.606 | 4.2 | 40 | 0.24346 | 92.8887 | 6506.2332
1798 | 3.3401 | 0 | 0 | 94.4929 | 88.9377 | 101494.229 | 20 | 22.5387 | 26.5729 | 27.7051 | 89.5692 | 79.428 | 4.2 | 40 | 0.24755 | 94.0075 | 6609.8528
1800 | 3.3268 | 0 | 0 | 94.3525 | 91.3343 | 101499.5027 | 20 | 22.5316 | 26.5638 | 27.7292 | 89.4327 | 79.34 | 4.2 | 40 | 0.24657 | 93.5857 | 6589.5732
1802 | 3.3302 | 0 | 0 | 96.8053 | 93.5867 | 101498.7477 | 20 | 22.5146 | 26.5769 | 27.7192 | 89.5431 | 79.377 | 4.2 | 40 | 0.24682 | 94.383 | 6639.3956